## Summary
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities — COMBINED CONTRACT SUMMARY
Employer: Ministry of Environment and Climate Change (MOECC), Federal Government of Somalia — UGBAAD Project (GCP/SOM/083/GCF), GCF/FAO
PART | DESCRIPTION | AMOUNT (USD)
PART A — JOWHAR IMC, Hirshabelle State
A0–A1 | Design and Works | 0
A2 | Supplies (hardware, software and tools) | 0
A3 | Furniture | 0
A4 | Installation and integration | 0
A5 | Services (testing, commissioning, documentation, maintenance support) | 0
A6 | Training | 0
| SUB-TOTAL PART A — JOWHAR | 0
PART B — KISMAYO IMC, Jubaland State
B0–B1 | Design and Works | 0
B2 | Supplies (hardware, software and tools) | 0
B3 | Furniture | 0
B4 | Installation and integration | 0
B5 | Services (testing, commissioning, documentation, maintenance support) | 0
B6 | Training | 0
| SUB-TOTAL PART B — KISMAYO | 0
C | PART C — GENERAL ITEMS AND PRELIMINARIES (both sites) | 0
| TOTAL (Parts A + B + C) | 0
| Contingency and provisional sums (5% of total — retained from original BOQ; Employer to confirm whether a contingency is to be carried in a lump-sum Contract) | 0
| GRAND TOTAL CONTRACT PRICE (USD) — to be carried to Form TEN-1 (lump sum, inclusive of all taxes and duties) | 0
NOTES
1. Amounts shown are computed only where both quantity and rate are numeric. Cells shaded yellow are quantities or rates not yet available (TBC) — the Grand Total is therefore INCOMPLETE until Annex B quantities/specifications are inserted and Bidders price all items.
2. Rates shown in blue are the rates from the original BOQ, retained where the item is unchanged; items marked 'REVIEW' in the status column have had their scope changed and their rates must be re-confirmed.
3. Building quantities for Kismayo are a copy of the Jowhar (original) building quantities: the original BOQ covered one building only. The Employer must confirm that the same concept design applies at both sites.
4. The Solar System bill in the original BOQ has been removed in full — solar PV is excluded from the Contract (Tender 6.3, 6.9).
5. Part A/B item lettering restarts within each element; page references (1/1/1 etc.) from the original BOQ are superseded by sheet names.
6. The 'Alignment note / status' column is for the Employer's review and should be deleted before the BOQ is issued to Bidders.

## Part C - Preliminaries
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART C — GENERAL ITEMS AND PRELIMINARIES (both sites)
Original Bill No. 2 General Matters retained; terminology aligned to the Tender (Supervisor, USD); items required by ITT/GCC/SCC/Section 6 added.
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
C1 GENERAL MATTERS (retained from original BOQ, terminology aligned)
A | Sufficiency of Tender: the Contractor shall be deemed to have satisfied himself before tendering as to the correctness and sufficiency of his Tender for the Works and of the rates and prices in the priced Bills of Quantities and Annex B, which shall cover all obligations under the Contract, including both the Jowhar and Kismayo sites. | 1 | ITEM | 0 | 0 | Modified: wording 'Architect' → 'Supervisor'; both sites
B | Stamp charges in connection with the Contract Agreement. | 1 | ITEM | 0 | 0 | Aligned
C | Definitions: 'Approved' and 'as directed' mean by the Supervisor; CM = cubic metre; SM = square metre; LM = linear metre; NO = number; KG = kilogramme; ITEM/LUMP = lump sum; 'Ditto' = the whole of the preceding description except as qualified. Standards: the Employer's Requirements, then Somali regulations where they exist, then ISO/IEC or equivalent national standards (Tender 6.4). | 1 | ITEM | 0 | 0 | Modified: 'Architect' and 'B.S.' definitions aligned to Tender 6.4 precedence
D | Programme of Works: baseline programme within 7 days of Commencement (SCC 4.5) with separate Jowhar and Kismayo workstreams, design/approval periods and equipment lead times; monthly updates. | 1 | ITEM | 0 | 0 | Modified: replaces 'Progress Schedule'; period per SCC
E | Provisional work: leave provisional/adjustable work uncovered for measurement by the Supervisor; uncover at own cost if in default. | 1 | ITEM | 0 | 0 | Aligned
F | Temporary lighting and power for the Works at both sites, including temporary connections, fees and permits, and clearing away on completion. | 2 | SITE | 0 | 0 | Quantity Revised: original 1 lump (one site) → 2 sites; rate retained per site — REVIEW
G | Water for the Works at both sites, including temporary storage, metered connection where available, fees and permits. | 2 | SITE | 0 | 0 | Quantity Revised: as above
H | Existing services: ascertain position of existing services before commencement; protect and make good. | 1 | ITEM | 0 | 0 | Aligned
I | Transport of materials, plant, Equipment, Furniture and workmen to and from the Jowhar and Kismayo sites, by permitted routes and hours, including security-related routing (Annex 10). All unit rates for local or imported goods include freight, insurance, handling, delivery to site, import duties, taxes and port charges (TDS 2.12: prices inclusive of all taxes). | 2 | SITE | 0 | 0 | Quantity Revised: original 1 lump → 2 sites; rate retained per site — REVIEW
J | Public and private roads and pavements: make good damage caused. | 1 | ITEM | 0 | 0 | Aligned
K | Compliance with Federal Government of Somalia laws, orders and regulations on employment of labour, insurance, pensions, holidays, safety, health and welfare; provision of PPE (helmet, overalls, boots) to all workers — enforced by the Employer. | 1 | ITEM | 0 | 0 | Aligned
L | Security of the Works, stores, materials, plant and personnel at each site, including watching and lighting. | 1 | ITEM | 0 | 0 | Aligned
M | Overtime working: at the Contractor's cost unless instructed in writing by the Supervisor. | 1 | ITEM | 0 | 0 | Modified: 'Architect' → 'Supervisor'
N | Materials and workmanship generally: all materials new and of the best quality; overseas materials ordered immediately after Contract signature; the BOQ shall not be used for ordering materials. | 1 | ITEM | 0 | 0 | Aligned
O | Site levels and setting out by a qualified surveyor; agree bench mark with the Supervisor; correct errors at own cost. | 1 | ITEM | 0 | 0 | Modified: Tender 6.8 requires a qualified surveyor
P | Rejected workmanship or materials: remove and replace at own cost. | 1 | ITEM | 0 | 0 | Aligned
Q | Samples and material approvals: submit sources and samples of cement, aggregate, reinforcement, blocks, roofing, finishes, electrical, ICT materials and furniture (catalogues, finish samples, one physical sample of each principal furniture item) before ordering (Tender 6.13, 6.15). | 1 | ITEM | 0 | 0 | Modified: furniture and equipment samples added per Tender 6.13/6.15
R | Concrete tests: making, curing, transport and crushing of cubes by an approved testing authority and obtaining certificates — set of forty 150 x 150 x 150 mm cubes per site. | 2 | SET | TBC |  | Quantity Revised: one set per site; rate not in original — TBC
S | Areas to be occupied by the Contractor: obtain the Supervisor's approval for siting of temporary buildings, spoil heaps, roads and storage. | 1 | ITEM | 0 | 0 | Aligned
T | Contractor's offices and secure, dry, weathertight storage sheds for materials, Equipment and Furniture at each site, floors at least 150 mm above ground; provide and maintain one level, levelling staff and one 30 m steel tape for the Supervisor. | 2 | SITE | TBC |  | Modified: secure dry storage for Equipment/Furniture per SCC mobilisation; rate not in original — TBC
U | Office for the Supervisor at each site: lock-up, weatherproof, with floor, lined walls and ceiling, glazed windows not less than 2 m², door with lock, table, chairs, drawing table and drawers; services and cleaning; removal on completion. | 2 | SITE | TBC |  | Modified: 'consultants' → 'Supervisor'; one per site; rate TBC
V | Telephone / mobile communication for the period of the Works, fees and rentals. | 1 | ITEM | TBC |  | Aligned: rate TBC
W | Sanitation: latrines for staff and workmen at each site to the satisfaction of the health authorities, maintained clean and removed on completion. | 2 | SITE | TBC |  | Aligned: rate TBC
X | Plant, tools and scaffolding for the due completion of the Works; scaffolding is not measured hereinafter. | 1 | ITEM | 0 | 0 | Aligned
Y | Signboard at each site of approved size and design displaying the Employer (MOECC), the UGBAAD Project, FAO and GCF, the Supervisor and the Contractor; no other advertisements without written approval. | 2 | NO | TBC |  | Modified: names aligned to Employer/Project; one per site; rate TBC
Z | Watching and lighting to safeguard the Works, plant and materials. | 1 | ITEM | 0 | 0 | Aligned
AA | Temporary roads and access to each site, including temporary culverts and crossings; removal and reinstatement on completion. Jowhar: allow for access during the Gu and Deyr rainy seasons (Tender 6.7). | 1 | ITEM | 0 | 0 | Modified: Jowhar rainy-season access added
AB | Existing and adjacent property: safeguard, make good and indemnify the Employer. | 1 | ITEM | 0 | 0 | Aligned
AC | Nuisance: minimise dust, noise, vibration and other nuisance to occupiers of adjacent properties (Tender 6.14). | 1 | ITEM | 0 | 0 | Aligned
AD | Specialist subcontractors (design, electrical, ICT, fire suppression, precision cooling, borehole): the Contractor remains fully responsible; subcontracting of the whole Works or the main structural works is not permitted (SCC). | 1 | ITEM | 0 | 0 | Modified: replaces 'Nominated Sub-contractors / Nominated Suppliers / P.C. sums' — no nominated subcontractors or P.C. sums exist in the Tender
AE | Protection of completed works and unfixed materials, including from rain, until Taking-Over. | 1 | ITEM | 0 | 0 | Aligned
AF | Protection of existing trees and vegetation; no tree to be cut without written instruction (Tender 6.14). | 1 | ITEM | 0 | 0 | Aligned
AG | Cleaning: remove surplus materials, plant and rubbish; clean floors, windows and finishes; leave the site clean at completion; packaging of Furniture and Equipment removed from site (Tender 6.13). | 1 | ITEM | 0 | 0 | Modified: packaging removal added
AH | Local regulations and by-laws: comply, serve notices and pay fees. | 1 | ITEM | 0 | 0 | Aligned
AI | Taxes: all applicable taxes, duties and levies are included in the rates (TDS 2.12). | 1 | ITEM | 0 | 0 | Modified: aligned to TDS: prices inclusive of all taxes
AJ | Fair wages and timely payment of labour; posting of conditions of employment in languages workers understand; compliance by subcontractors. | 1 | ITEM | 0 | 0 | Aligned
| TOTAL — C1 General matters — CARRIED TO COLLECTION |  |  |  | 0
C2 ITEMS REQUIRED BY THE TENDER DOCUMENT (added)
A | Mobilisation and site establishment at both sites, including the mobilisation plan and demobilisation (SCC — Mobilisation; payment milestone 1). | 1 | ITEM | TBC |  | Added: Tender SCC mobilisation clause; rate TBC
B | Performance Security (10% of Contract Price, bank guarantee, valid to 28 days after end of DLP) and Advance Payment Guarantee (TDS 2.31, SCC 4.9) — bank charges. | 1 | ITEM | TBC |  | Added: TDS 2.31; rate TBC
C | Insurances: Works, Goods in transit and on site, Contractor's Equipment (full replacement value); third-party liability not less than USD 500,000 per occurrence; workers' compensation/employer's liability (SCC 4.13). | 1 | ITEM | TBC |  | Added: SCC 4.13; rate TBC
D | Health, Safety, Environment and Social (HSES) Plan and Contractor's Environmental and Social Management Plan (C-ESMP) per site; HSE Officer at each site; risk assessments, toolbox talks, first aid, emergency plan, incident reporting; worker code of conduct, PSEA and child-protection training; community liaison and grievance mechanism with monthly log (Tender 6.14). | 2 | SITE | TBC |  | Added: Tender 6.14 / SCC safeguards; rate TBC
E | Environmental management: dust, noise, waste, wastewater, fuel/oil and hazardous-materials management; bunding at fuel storage; erosion and sediment control; chance-finds procedure (Tender 6.14). | 2 | SITE | TBC |  | Added: Tender 6.14; rate TBC
F | Security compliance at each site: personnel accreditation, movement notification/clearance, approved transport, security briefings per Annex 10 (SCC — Security). | 2 | SITE | TBC |  | Added: SCC security / Annex 10; rate TBC
G | Quality Assurance / Quality Control Plan with Inspection and Test Plan per site, hold and witness points, non-conformance reporting (Tender 6.15). | 1 | ITEM | TBC |  | Added: Tender 6.15; rate TBC
H | Reporting: inception report, weekly site meetings and minutes, monthly progress reports per site with photographs, site diary and daily returns, completion report (Tender 6.20). | 1 | ITEM | TBC |  | Added: Tender 6.20; rate TBC
I | Key Personnel: Project Manager; full-time Site Engineer, Foreman and HSE Officer at each site; Electrical/ICT Engineer covering both sites; Architect and Structural Engineer for design (Tender 3.1, SCC) — for the duration of the Contract. | 1 | ITEM | TBC |  | Added: Tender 3.1 / SCC Key Personnel; rate TBC
J | Provisional Sum for geotechnical/soil investigation at either site where no report is issued with the Tender (Tender 6.8) — to be expended only as instructed by the Supervisor. | 1 | PS | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED — amount of provisional sum to be set by Employer
K | Permits: building permit, land documentation and borehole permit obtained by the Employer with the State authorities; electricity and water connections and import/customs clearance arranged and paid by the Contractor (Tender 6.22). | 1 | ITEM | TBC |  | Added: Tender 6.22; rate TBC
| TOTAL — C2 Tender-required items — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART C — GENERAL ITEMS AND PRELIMINARIES
| C1 General matters |  |  |  | 0
| C2 Tender-required items |  |  |  | 0
| TOTAL — PART C — GENERAL ITEMS AND PRELIMINARIES — CARRIED TO SUMMARY |  |  |  | 0

## A0-A1 Jowhar Design&Works
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART A — JOWHAR IMC — A0 DETAILED DESIGN AND A1 WORKS (Component A: Design and Works)
Quantities are the Employer's indicative quantities for a single-storey IMC taken from the original BOQ (one building); the Contractor verifies them against its approved design (design-and-build, Tender 6.3). Jowhar, Hirshabelle State (riverine — Shabelle flood plain): finished floor level set to the flood risk in the site survey; foundations for expansive/weak alluvial soils per geotechnical report; damp-proofing and termite protection; rainy-season access (Tender 6.7).
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
A0 DETAILED DESIGN (Tender 6.3, SCC 4.4)
A | Detailed architectural design: site layout, floor plans, elevations, sections, schedule of finishes, doors/windows, furniture layout, signage — signed by the registered Architect; submission within 21 days of Commencement and revisions until approval. | 1 | ITEM | TBC |  | Added: Tender 6.3 (design-and-build); rate TBC
B | Structural design: foundations based on the geotechnical report, superstructure, roof structure, calculations and design basis report — signed by the Structural Engineer. Flood-plain levels and alluvial soils. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
C | Electrical design: load schedule, single-line diagram, distribution, lighting, earthing and lightning protection, generator/ATS/UPS sizing and layout. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
D | Mechanical design: air-conditioning and precision-cooling loads and layouts, fire detection/suppression, plumbing, water supply, sanitation and stormwater drainage. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
E | ICT design: structured-cabling layout, server-room layout, network architecture, CCTV and access-control layouts, hardware/software configuration for a fully functional IMC. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
F | External-works design: perimeter security, guard post, car park, landscaping, drainage; shop drawings, coordination drawings, temporary-works design and as-built drawings. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
| TOTAL — A0 Detailed design — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 1 — SUBSTRUCTURE (all work up to and including the ground-floor slab)
A | Clear site of grass, shrubs, bush and small trees; grub up roots; fill with selected soil; remove debris to an approved dump (no burning — Tender 6.14 environmental management). | 768 | SM | 0 | 0 | Modified: 'burn debris' removed (environmental requirement)
B | Excavate for column bases not exceeding 1.5 m from reduced level. | 89 | CM | 0 | 0 | Aligned
C | Excavate for foundation trench not exceeding 1.5 m deep from reduced level. | 195 | CM | 0 | 0 | Aligned
D | Return, fill and ram selected excavated material around foundations and below ground slabs in layers not exceeding 200 mm, compacted to 95% MDD. | 114 | CM | 0 | 0 | Aligned
E | Surplus excavated material: load, wheel, spread and level on site where directed. | 170 | CM | 0 | 0 | Aligned
F | 200 mm hardcore bed in broken stone minimum 75 mm, blinded, under floor bed and verandah. | 113.71 | CM | 0 | 0 | Aligned
G | Ditto, 100 mm under steps, ramps and landings (step-free access — Tender 6.6). | 5.3 | CM | 0 | 0 | Aligned
H | 50 mm sand blinding over hardcore. | 465 | SM | 0 | 0 | Aligned
I | Anti-termite treatment (Termidor EC 25 or equal and approved) to hardcore surfaces, top of foundation walling, excavation bottoms and sides, and made-up ground (Tender 6.7/6.8 termite protection). | 623 | SM | 0 | 0 | Aligned
| PLAIN IN-SITU CONCRETE CLASS 20 (min. mix 1:2:4, 20 mm aggregate, 0.5 w/c) in: |  |  | 0
J | 50 mm blinding under column bases and strip footings and to make up levels. | 95 | SM | 0 | 0 | Aligned
| VIBRATED IN-SITU REINFORCED CONCRETE CLASS 20 (20 mm aggregate, 0.5 w/c, min. 400 kg cement/m³) in: |  |  | 0
K | Column bases. | 22 | CM | 0 | 0 | Aligned
L | Strip footings. | 33 | CM | 0 | 0 | Aligned
M | Stub columns. | 2.48 | CM | 0 | 0 | Aligned
N | Ground beams. | 32 | CM | 0 | 0 | Aligned
O | 600 mm wide splash apron. | 52 | SM | 0 | 0 | Aligned
STEEL FABRIC REINFORCEMENT (A142 mesh, 2.22 kg/m²) in floor bed, verandah, splash aprons, ramps, landings, steps and stormwater channel, including tying wire and spacers:
P | A142 fabric mesh. | 631 | SM | 0 | 0 | Aligned
MILD STEEL ROUND BARS / HIGH-TENSILE RIBBED BARS, cut, bent, fixed:
Q | 8 mm diameter mild steel bars. | 1602 | KG | 0 | 0 | Aligned
R | 12 mm diameter high-tensile ribbed bars. | 3055 | KG | 0 | 0 | Aligned
FORMWORK to:
S | Sides of column bases. | 86 | SM | 0 | 0 | Aligned
T | Sides of strip footings. | 108 | SM | 0 | 0 | Aligned
U | Sides of stub columns. | 49 | SM | 0 | 0 | Aligned
V | Sides of ground beams. | 158 | SM | 0 | 0 | Aligned
W | Vertical sides of ramp and landing, average 125 mm wide, cut to profile. | 3 | SM | 0 | 0 | Aligned
X | Vertical sides of steps, average 150 mm girth. | 8 | SM | 0 | 0 | Aligned
DAMP-PROOF MEMBRANE (Tender 6.7/6.8 damp-proofing):
Y | 1000-gauge polythene DPM in one layer with 300 mm laps on blinded hardcore to floor bed, verandah, splash apron, ramps and landings. | 615 | SM | 0 | 0 | Aligned
WALLING below ground:
Z | 400 mm thick approved natural stone foundation walling in cement/sand (1:3) mortar. | 126.24 | CM | 0 | 0 | Aligned
| TOTAL — Element 1 Substructure — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 2 — REINFORCED CONCRETE FRAME
VIBRATED IN-SITU REINFORCED CONCRETE CLASS 20 (20 mm aggregate, min. 400 kg cement/m³) in:
A | Roof/ring beams. | 13 | CM | 0 | 0 | Aligned
B | Lintels. | 5.9 | CM | 0 | 0 | Aligned
C | Columns. | 7 | CM | 0 | 0 | Aligned
STEEL REINFORCEMENT, cut, bent, hoisted and fixed, including tying wire and spacers:
D | 8 mm diameter mild steel bars. | 961 | KG | 0 | 0 | Aligned
E | 12 mm diameter high-tensile ribbed bars. | 1226 | KG | 0 | 0 | Aligned
F | 14 mm diameter high-tensile ribbed bars. | 1016 | KG | 0 | 0 | Aligned
FORMWORK to:
G | Sides and soffits of ring/roof beams. | 252 | SM | 0 | 0 | Aligned
H | Sides and soffits of lintels. | 118 | SM | 0 | 0 | Aligned
I | Sides of columns. | 134 | SM | 0 | 0 | Aligned
| TOTAL — Element 2 RC frame — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 3 — WALLING
Solid concrete blockwork 5.0 N/mm² (samples and laboratory test results before proceeding — Tender 6.15 material approvals), jointed and pointed in cement/sand (1:4) mortar, with double hoop-iron ties every fourth course (Tender 6.8 concrete-block walling):
A | 200 mm thick walls. | 493 | SM | 0 | 0 | Aligned
B | 200 mm concrete vent blocks (3.5 N/mm²) bedded, jointed and pointed in cement/sand (1:4) mortar, finished in coloured cement. | 11 | SM | 0 | 0 | Aligned
| TOTAL — Element 3 Walling — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 4 — ROOFING, CEILING AND RAINWATER DISPOSAL
TIMBER TRUSSES — rates include gusset and base plates, stiffeners, bolts, cleats, drilling, concrete pockets, connections, treatment and painting, per the Contractor's approved structural design; trusses engineered for wind uplift; samples approved before mass production. The following in 4 No. trusses spanning approx. 9000 mm hoisted approx. 3500 mm above ground (Tender 6.8: steel or treated-timber trusses):
A | 150 x 50 mm treated top chords. | 344.4 | LM | 0 | 0 | Modified: 'treated' timber per Tender 6.8
B | 150 x 50 mm treated tie beams. | 299.4 | LM | 0 | 0 | Aligned
C | 150 x 50 mm treated ridge and valley members. | 228.8 | LM | 0 | 0 | Aligned
D | 100 x 50 mm treated struts and ties. | 244.7 | LM | 0 | 0 | Aligned
E | 100 x 50 mm purlins including 150 x 100 x 5 mm MS cleats on trusses. | 878.4 | LM | 0 | 0 | Aligned
F | 100 x 50 mm wall plate. | 146 | LM | 0 | 0 | Aligned
G | 200 x 200 x 5 mm MS plates with 4 holes for 16 mm anchor bolts. | 36 | NO | 0 | 0 | Aligned
H | 50 x 150 x 4 mm plates with 50 x 200 x 4 mm split cleats anchored into concrete pockets. | 36 | NO | 0 | 0 | Aligned
I | 12 mm diameter grade 4.6 anchor bolts 385 mm long with nuts and washers. | 36 | NO | 0 | 0 | Aligned
ROOF COVERING — 28-gauge pre-painted IT5 profiled metal roofing sheets fixed to purlins with J-bolts:
J | Sheeting laid sloping not exceeding 45° from horizontal. | 878 | SM | 0 | 0 | Aligned
K | Ridge capping to match. | 114.8 | LM | 0 | 0 | Aligned
L | Under-roof insulation to reduce internal heat gain (Tender 6.8) — reflective foil/insulation laid over purlins under sheeting. | 878 | SM | TBC |  | Added: Tender 6.8 under-roof insulation; qty taken as roof area; rate TBC
M | 200 x 25 mm wrot cypress fascia and barge boards fixed to trusses, three coats paint. | 168 | LM | 0 | 0 | Aligned
N | Ceiling: 1200 x 2400 x 6 mm commercial plywood panels fixed to trusses, three coats paint — to all rooms except the server room. | 448 | SM | 0 | 0 | Modified: 'for classrooms' (school template) → 'all rooms'; panel size 240 mm corrected to 2400 mm — REVIEW
O | Server-room ceiling: sealed, dust-free ceiling (e.g. moisture-resistant gypsum board, taped, sealed and painted), no water services above (Tender 6.8). | TBC | SM | TBC |  | Added: Tender 6.8 server-room finishes; area NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
RAINWATER DISPOSAL — uPVC gutters, downpipes and fittings (Marley or equal and approved) discharging to the stormwater drainage system (Tender 6.8):
P | 150 mm diameter gutters complete with brackets to timber fascia. | 166 | LM | 0 | 0 | Aligned
Q | Extra over for 150 mm gutter angles and swan-necks. | 16 | NO | 0 | 0 | Aligned
R | Extra over for 150 mm stop ends. | 14 | NO | 0 | 0 | Aligned
S | Extra over for 150 x 110 mm gutter outlets. | 28 | NO | 0 | 0 | Aligned
T | 110 mm diameter uPVC downpipes clipped to walls, cast below splash apron at bottom. | 60 | LM | 0 | 0 | Aligned
U | Extra over for 110 mm x 90° bends. | 10 | NO | 0 | 0 | Aligned
V | Extra over for 110 mm shoes cast below splash apron. | 10 | NO | 0 | 0 | Aligned
Prepare, prime and apply three coats gloss oil paint to:
W | Surfaces over 200 mm not exceeding 300 mm girth (fascia). | 200 | LM | 0 | 0 | Aligned
X | Surfaces not exceeding 100 mm girth. | 50 | LM | 0 | 0 | Aligned
Y | 110 mm diameter uPVC downpipes. | 50 | LM | 0 | 0 | Aligned
Z | Extra over for bends. | 56 | NO | 0 | 0 | Requires Review: 56 bends vs 10 bends in item above — original BOQ inconsistency
AA | Extra over for shoes. | 18 | NO | 0 | 0 | Requires Review: 18 shoes vs 10 shoes above — original BOQ inconsistency
| TOTAL — Element 4 Roofing and rainwater — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 5 — DOORS (Tender 6.8: security grilles/shutters and insect screening; solid-core/steel doors with access-controlled locks to server room and archive; fire-rated doors where required)
A | Main-entrance aluminium-framed glazed double doors with safety glazing, frames, handles, locks, hinges, closers and ironmongery, complete. | 2 | NO | 0 | 0 | Aligned
B | Internal flush doors with hardwood/metal frames, architraves, hinges, lever handles, locks, stops and ironmongery, complete. | 14 | NO | 0 | 0 | Aligned
C | Fire-rated steel door and frame to the server room with fire-rated hardware, closer, lever hardware and lockset, prepared for the electronic access-control lock (Tender 6.8/6.9). | 1 | NO | 0 | 0 | Modified: prepared for access control per Tender 6.9
D | Solid-core or steel door and frame to the archive/records room with lockset, prepared for the electronic access-control lock (Tender 6.8/6.9). | 1 | NO | TBC |  | Added: Tender 6.8 archive door; rate TBC
E | External security shutters/grilles to external doors where required by the approved design. | TBC | SM | TBC |  | Added: Tender 6.8; extent NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 5 Doors — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 6 — WINDOWS
A | Powder-coated aluminium-framed glazed windows, sliding/casement, with clear glazing, handles, locks, stays, seals, perimeter sealant and accessories, complete. | 78 | SM | 0 | 0 | Aligned
B | Burglar-proof steel security grilles to windows/openings, welded, anti-corrosion treated and painted, complete. | 38 | SM | 0 | 0 | Aligned
C | Insect screening to all openable windows and external doors (Tender 6.8) — aluminium/fibreglass mesh in frames. | 78 | SM | TBC |  | Added: Tender 6.8; qty taken as window area; rate TBC
| TOTAL — Element 6 Windows — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 7 — WALL FINISHES
EXTERNAL — cement and washed sand (1:3) render, trowelled smooth:
A | 20 mm two-layer render to walls with flattened tyrolean finish in cement/washed sand (1:2). | 327 | SM | 0 | 0 | Aligned
B | Ditto to external skirting, average 200–300 mm wide. | 141 | LM | 0 | 0 | Aligned
EXTERNAL PAINTING — prepare and apply three coats first-grade weatherguard emulsion (waterproofing and damp-proofing appropriate to the climate — Tender 6.8):
C | Rendered/tyrolean walls and concrete surfaces. | 327 | SM | 0 | 0 | Unit Revised: LM → SM (area = render area)
D | Skirting 200–300 mm girth, external. | 141 | LM | 0 | 0 | Aligned
INTERNAL LIME PLASTER — first coat cement/lime/sand (1:2:9), second coat cement/lime putty/sand (1:1:6), steel-trowelled smooth:
E | 12 mm two-coat plaster to walls. | 624 | SM | 0 | 0 | Unit Revised: LM → SM
F | Plaster to internal skirting 200–300 mm girth. | 252 | LM | 0 | 0 | Unit Revised: SM → LM
INTERNAL PAINTING — one mist coat and three coats silk vinyl emulsion on:
G | Plastered wall surfaces. | 624 | SM | 0 | 0 | Aligned
H | Skirting 200–300 mm girth, internal. | 252 | LM | 0 | 0 | Aligned
I | Server room: sealed, dust-free wall finish — anti-dust epoxy/acrylic sealer coating over plaster (Tender 6.8). | TBC | SM | TBC |  | Added: Tender 6.8; area NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 7 Wall finishes — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 8 — FLOOR FINISHES
VIBRATED IN-SITU REINFORCED CONCRETE CLASS 20 in:
A | 125 mm thick ground-floor slab. | 83.13 | CM | 0 | 0 | Aligned: original formula 665 SM x 0.125 retained
B | Extra over floor bed for 25 mm power-floated topping with hardener, bonding agent and 25 mm ebonite strips at 2 x 2 m grid — floors generally, verandah, ramps and steps. | 665 | SM | 0 | 0 | Aligned
C | 150 x 25 mm cement/sand (1:3) verandah skirting, square top and coved bottom. | 53 | LM | 0 | 0 | Aligned
D | Ceramic floor tiles on cement/sand screed with matching skirting, to offices, reception, meeting/training room, corridors and sanitary areas per Schedule of Finishes. | 200 | SM | 0 | 0 | Modified: now included in element total (was excluded from original SUM range)
E | Raised access floor to the server room: 600 x 600 mm steel-encapsulated panels on adjustable pedestals, anti-static HPL finish, ramp/step at threshold, cut-outs for cabling (Tender 6.6/6.8). | TBC | SM | TBC |  | Added: Tender 6.8 raised floor; area NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 8 Floor finishes — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 9 — ELECTRICAL INSTALLATION WORKS (Tender 6.9). Generator, ATS and UPS are supplied under Part A2 and installed/commissioned under Parts A4/A5.
All materials supplied, delivered, installed, connected, tested and commissioned complete with fixing, mounting and terminating accessories per the approved design; suitable for the 415/240 V 50 Hz system; underground cables include excavation, sand bedding, ducts and backfilling; indoor cables concealed in conduits/trunking; fire detection fully addressable; installation tested to IEC 60364 / current IET Wiring Regulations (Tender 6.4) and witnessed by the Supervisor.
A | Connection to the mains supply as shown on the electrical Drawings, including metering, main incomer and supply-authority requirements (Tender 6.9). | 1 | ITEM | TBC |  | Added: Tender 6.9 mains connection; availability per Annex G; rate TBC
B | Main LV distribution board (MDB) with MCCBs, MCBs, residual-current protection, surge protection, busbars, metering, enclosure and accessories, with ATS incomer provision. | 1 | NO | 0 | 0 | Modified: RCD protection added per Tender 6.9
C | Sub-distribution boards with breakers, RCDs, surge protection, busbars, neutral/earth bars and accessories — including a dedicated UPS-fed board for the server room, cooling and ICT equipment (Tender 6.9 dedicated circuits). | 3 | NO | 0 | 0 | Modified: dedicated server-room/UPS board included in 3 No. — REVIEW
D | Distribution-board feeder cables with glands, lugs, terminations and supports. | 1 | ITEM | 0 | 0 | Unit Revised: NO → ITEM
E | Cable containment: trunking and cable trays with supports and accessories, separate from ICT containment. | 150 | M | 0 | 0 | Aligned
POWER AND SOCKET OUTLETS:
F | Twin 13 A switched socket outlets, flush, with wiring and accessories. | 50 | NO | 0 | 0 | Aligned
G | Dedicated 13 A socket outlets for IT/server equipment on UPS-fed circuits. | 20 | NO | 0 | 0 | Modified: UPS-fed per Tender 6.9
H | Weatherproof external socket outlets. | 6 | NO | 0 | 0 | Aligned
I | Isolator switches for dedicated equipment (AC units, precision cooling, pumps). | 10 | NO | 0 | 0 | Aligned
| LIGHTING (internal LED lighting, external and perimeter security lighting — Tender 6.9): |  |  | 0
J | LED recessed/panel light fittings approx. 36–40 W with drivers and accessories. | 70 | NO | 0 | 0 | Aligned
K | LED surface-mounted light fittings for service areas. | 20 | NO | 0 | 0 | Aligned
L | LED external/security light fittings to building perimeter. | 12 | NO | 0 | 0 | Aligned
M | LED perimeter/fence security lighting on poles or wall brackets with photocell control (Tender 6.6/6.9). | TBC | NO | TBC |  | Added: Tender 6.6 perimeter external lighting; qty NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
N | Lighting switches, 1-way/2-way as required. | 25 | NO | 0 | 0 | Aligned
O | Lighting control wiring, conduits and accessories. | 1 | ITEM | 0 | 0 | Aligned
WIRING AND CONDUITING:
P | PVC/LSZH conduits, concealed or surface, with bends, boxes, saddles and accessories. | 1000 | M | 0 | 0 | Aligned
Q | Lighting-circuit wiring complete with cables, conduits and terminations. | 1200 | M | 0 | 0 | Aligned
R | Socket/power-circuit wiring complete with cables, conduits and terminations. | 1500 | M | 0 | 0 | Aligned
S | Sub-main cables between MDB and distribution boards. | 300 | M | 0 | 0 | Aligned
T | Cable glands, lugs, ferrules, connectors, junction boxes and miscellaneous accessories. | 1 | ITEM | 0 | 0 | Requires Review: USD 10,000 lump for sundries appears high relative to the installation — REVIEW rate
GENERATOR AND ATS BUILDER'S WORK AND CABLING (equipment under Part A2):
U | Generator-to-ATS/MDB power cable, glands, lugs and terminations. | 1 | ITEM | 0 | 0 | Aligned
V | Reinforced-concrete generator plinth, secure ventilated enclosure/canopy base, exhaust routing and bunded fuel-storage area (Tender 6.9). | 1 | ITEM | TBC |  | Added: Tender 6.9 generator location; rate TBC
EARTHING AND LIGHTNING PROTECTION (Tender 6.9):
W | Main building earthing system: electrodes, earth pits, copper/GI conductors and connections. | 1 | ITEM | 0 | 0 | Aligned
X | Dedicated clean earth for the server room and ICT equipment, bonded to the main earth (Tender 6.9). | 1 | ITEM | TBC |  | Added: Tender 6.9 clean earth; rate TBC
Y | Equipotential bonding to MDB, DBs and metallic services. | 1 | ITEM | 0 | 0 | Aligned
Z | Lightning-protection system: air terminals, down conductors, earth electrodes, test clamps and accessories. | 1 | ITEM | 0 | 0 | Aligned
EMERGENCY AND SAFETY LIGHTING:
AA | Emergency LED fittings with integral battery backup. | 15 | NO | 0 | 0 | Aligned
AB | Illuminated EXIT signs with battery backup (fire-exit signage — Tender 6.9). | 8 | NO | 0 | 0 | Aligned
AC | External emergency/security lighting and controls. | 1 | ITEM | 0 | 0 | Aligned
| TOTAL — Element 9 Electrical works — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 10 — WATER SUPPLY, SANITATION AND DRAINAGE (Tender 6.10)
A | Borehole: drilling, casing, screening, gravel pack, development and test pumping, wellhead, submersible pump, rising main, cabling and controls, with water-quality test — where the borehole is the water source per the mechanical Drawings. | 1 | NO | TBC |  | Added: Tender 6.10; depth/yield NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED; delete if network connection applies
B | Connection to the municipal/private water network with meter and isolation valve — where applicable per the mechanical Drawings. | 1 | ITEM | TBC |  | Added: Tender 6.10 alternative source; rate TBC
C | Water storage: elevated and/or ground storage tank(s) with support structure, booster/transfer pump, float controls, pipework and valves (Tender 6.6/6.10). | 1 | ITEM | TBC |  | Added: capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | Piped water supply: cold-water piping, valves, meters and fittings to sanitary facilities and external taps (retained from original 'Piped supply systems'). | 1 | ITEM | 0 | 0 | Modified: description aligned; rate retained but REVIEW (was a lump 'as per drawings')
E | Sanitary fittings: WCs, wash-hand basins, urinals, taps, mirrors, dispensers and accessories for male, female and accessible facilities, including accessible WC grab rails and step-free access (Tender 6.6/6.10). | 1 | SET | TBC |  | Added: numbers of fittings NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Foul drainage and disposal: sanitary drainage pipes, fittings, traps, manholes, cleanouts and septic tank with soakaway or connection to sewer as applicable (retained from original 'Disposal systems', aligned). | 1 | ITEM | 0 | 0 | Modified: septic tank/soakaway explicit; rate retained but REVIEW
G | Stormwater drainage: surface channels, gullies, pipes and outfall for roof, hardstanding and site — discharge to an approved outfall with levels set to flood risk (Tender 6.7 Jowhar). | 1 | ITEM | TBC |  | Added: Tender 6.10; extent NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 10 Water and sanitation — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 11 — EXTERNAL WORKS AND PERIMETER SECURITY (Tender 6.6/6.8)
A | Perimeter wall or fence to the height and type in the approved design. | TBC | LM | TBC |  | Added: type/height/length NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Vehicle gate, steel, with locks. | 1 | NO | TBC |  | Added: Tender 6.6; rate TBC
C | Pedestrian gate, steel, with lock. | 1 | NO | TBC |  | Added: Tender 6.6; rate TBC
D | Guard post / security screening point at the main gate, complete with finishes, door, window, lighting and power. | 1 | NO | TBC |  | Added: Tender 6.6; size NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Car park and hardstanding: sub-base, base and surfacing with kerbs and markings. | TBC | SM | TBC |  | Added: capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Paved paths and step-free access routes. | TBC | SM | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
G | Landscaping with drought-tolerant planting and topsoil. | TBC | SM | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
H | Building identification signage in English and Somali as instructed by the Employer (Tender 6.8). | 1 | NO | TBC |  | Added: rate TBC
| TOTAL — Element 11 External works — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART A0–A1 — JOWHAR DESIGN AND WORKS
| A0 Detailed design |  |  |  | 0
| Element 1 Substructure |  |  |  | 0
| Element 2 RC frame |  |  |  | 0
| Element 3 Walling |  |  |  | 0
| Element 4 Roofing and rainwater |  |  |  | 0
| Element 5 Doors |  |  |  | 0
| Element 6 Windows |  |  |  | 0
| Element 7 Wall finishes |  |  |  | 0
| Element 8 Floor finishes |  |  |  | 0
| Element 9 Electrical works |  |  |  | 0
| Element 10 Water and sanitation |  |  |  | 0
| Element 11 External works |  |  |  | 0
| TOTAL — PART A0–A1 — JOWHAR DESIGN AND WORKS — CARRIED TO SUMMARY |  |  |  | 0

## A2 Jowhar Supplies
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART A — JOWHAR IMC — A2 SUPPLIES: HARDWARE, SOFTWARE AND TOOLS (Component B)
All equipment new, of current production, supported by the manufacturer in the region, with manufacturer's warranty (min. 12 months), manuals and datasheets; licences in the Employer's name (Tender 6.12). Ratings and quantities per Annex B — where Annex B does not yet state them they are marked TBC.
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
A2.1 BACKUP POWER (Tender 6.9)
A | Standby diesel generator set, rating per Annex B, sound-attenuated canopy, automatic start on mains failure, control panel, starter battery, exhaust, base/day fuel tank of capacity per Annex B, and accessories. | 1 | NO | 0 | 0 | Modified: sound-attenuated canopy, auto-start and fuel tank added per Tender 6.9; rating not specified — rate REVIEW
B | Automatic transfer switch (ATS) with enclosure, controls and load-shedding provision for non-essential circuits. | 1 | NO | 0 | 0 | Aligned
C | UPS, on-line double-conversion, rating and autonomy per Annex B, sealed maintenance-free batteries, bypass and monitoring, for the server room and critical loads. | 1 | NO | TBC |  | Added: Tender 6.9; rating NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — A2.1 Backup power — CARRIED TO COLLECTION |  |  |  | 0
A2.2 AIR-CONDITIONING AND PRECISION COOLING (Tender 6.9)
A | Precision-cooling units for the server room sized to the IT heat load, N+1 redundancy, with temperature/humidity monitoring and alarms. | TBC | NO | TBC |  | Added: number/capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Split air-conditioning units for offices, workstation area, meeting/training room and reception, capacities per mechanical Drawings. | TBC | NO | TBC |  | Added: number/capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — A2.2 Cooling — CARRIED TO COLLECTION |  |  |  | 0
A2.3 FIRE DETECTION AND SUPPRESSION (Tender 6.9)
A | Addressable fire detection and alarm system: control panel at reception/guard post, detectors, manual call points, sounders, cabling and batteries, zoned per the approved design. | 1 | SET | TBC |  | Added: number of devices NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Clean-agent (gaseous) suppression system for the server room with cylinders, nozzles, pipework, pre-discharge warning, abort switch and interlocks to cooling and power; agent per mechanical Specifications. | 1 | SET | TBC |  | Added: agent/room volume NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Portable fire extinguishers of appropriate type with brackets and signage, to all areas. | TBC | NO | TBC |  | Added: number NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — A2.3 Fire — CARRIED TO COLLECTION |  |  |  | 0
A2.4 SECURITY SYSTEMS (Tender 6.9)
A | CCTV system: cameras covering perimeter, gates, entrances, reception, workstation area and server-room door; network video recorder with not less than 30 days' retention; monitoring display at guard post/reception; cabling and PoE. | 1 | SET | TBC |  | Added: number of cameras NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Electronic access-control system at the main entrance, server room and archive: controllers, readers, electric locks, door hardware, cards/credentials and software with audit logging. | 3 | DOOR | TBC |  | Added: Tender 6.9: three controlled doors; rate TBC
| TOTAL — A2.4 Security — CARRIED TO COLLECTION |  |  |  | 0
A2.5 SERVER ROOM, NETWORK AND ICT HARDWARE (Tender 6.11/6.12)
A | Lockable 42U server racks with PDUs fed from the UPS, cable management and accessories. | TBC | NO | TBC |  | Added: number NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Environmental monitoring (temperature, humidity, water leak, door) with alarms. | 1 | SET | TBC |  | Added: rate TBC
C | Rack servers. | TBC | NO | TBC |  | Added: specification/number NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | Network-attached storage or SAN. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Backup device/media. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Rack-mounted KVM. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
G | Core/distribution switches. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
H | Edge/access switches (PoE). | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
I | Firewall/router. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
J | Wi-Fi access points covering all working areas. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
K | Patch panels, patch cords and rack accessories. | 1 | SET | TBC |  | Added: rate TBC
L | GIS/data-processing workstations, high specification, with dual monitors. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
M | Office desktop computers with monitors. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
N | Laptops. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
O | Multifunction printers/copiers. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
P | Large-format plotter/scanner for maps (if required by Annex B). | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
Q | Document scanner. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
R | Meeting/training room AV: projector or large-format display, screen, sound system, video-conferencing unit. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — A2.5 ICT hardware — CARRIED TO COLLECTION |  |  |  | 0
A2.6 SOFTWARE AND LICENCES (Tender 6.11/6.12) — licences issued in the Employer's name
A | Server operating systems and client access licences. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Workstation operating systems. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Database software. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | GIS software (desktop and server) and data-analysis software. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Office productivity suite. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Antivirus/endpoint security. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
G | Backup software. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — A2.6 Software — CARRIED TO COLLECTION |  |  |  | 0
A2.7 TOOLS FOR DATA COLLECTION AND ANALYSIS (Tender 6.12)
A | Handheld GPS units. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Field data-collection tablets / rugged devices with protective cases. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Survey and measurement tools for field data collection. | TBC | SET | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | External storage drives and media. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — A2.7 Data-collection tools — CARRIED TO COLLECTION |  |  |  | 0
A2.8 SPARE PARTS AND CONSUMABLES (Tender 6.12/6.18)
A | Manufacturers' recommended spare parts and consumables for the first 12 months of operation for generator, UPS, cooling, fire, security and ICT systems, with spare-parts list and local supplier contacts. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — A2.8 Spares — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART A2 — JOWHAR SUPPLIES
| A2.1 Backup power |  |  |  | 0
| A2.2 Cooling |  |  |  | 0
| A2.3 Fire |  |  |  | 0
| A2.4 Security |  |  |  | 0
| A2.5 ICT hardware |  |  |  | 0
| A2.6 Software |  |  |  | 0
| A2.7 Data-collection tools |  |  |  | 0
| A2.8 Spares |  |  |  | 0
| TOTAL — PART A2 — JOWHAR SUPPLIES — CARRIED TO SUMMARY |  |  |  | 0

## A3 Jowhar Furniture
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART A — JOWHAR IMC — A3 FURNITURE AND OFFICE FITTINGS (Component C, Tender 6.13)
Commercial/office-grade furniture for continuous institutional use; laminated/veneered moisture-resistant tops with sealed edges; powder-coated steel or hardwood frames; cleanable upholstery; all cabinets/pedestals/lockers lockable with two keys, keyed differently and recorded in a key schedule; delivered assembled or assembled on site, levelled and fixed; min. 12-month warranty; every item asset-tagged. Quantities per Annex B / furniture layout — TBC where not yet stated.
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
A3.1 OFFICES (technical and administrative staff)
A | Office desk with lockable drawer pedestal. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Ergonomic office chair: height adjustment, tilt, lumbar support, armrests, swivel. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Visitor chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Lockable steel filing cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Bookshelf/storage cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.1 Offices (Technical And Administrative Staff) — CARRIED TO COLLECTION |  |  |  | 0
A3.2 GIS / DATA-PROCESSING WORKSTATION AREA
A | Staff workstation/computer table sized for dual monitors, with cable management and CPU holder. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Ergonomic operator chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Mobile pedestal, lockable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Shared lockable storage unit. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.2 Gis / Data-Processing Workstation Area — CARRIED TO COLLECTION |  |  |  | 0
A3.3 MEETING / TRAINING ROOM
A | Modular meeting/conference table for the number of persons on the furniture layout. | TBC | SET | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Meeting/training chairs, stackable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Presenter's table/lectern. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Whiteboard and flip-chart stand. | TBC | SET | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Storage cabinet for training materials. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.3 Meeting / Training Room — CARRIED TO COLLECTION |  |  |  | 0
A3.4 RECEPTION / WAITING AREA
A | Reception desk/counter with lockable storage. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Receptionist chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Visitor seating: waiting benches/sofa units. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Coffee table. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Notice board. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.4 Reception / Waiting Area — CARRIED TO COLLECTION |  |  |  | 0
A3.5 SERVER / ICT ROOM (racks are under Part A2)
A | Technician's worktable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Technician's stool/chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Lockable storage cabinet for ICT spares, tools and media. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Wall-mounted document holder for network documentation. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.5 Server / Ict Room (Racks Are Under Part A2) — CARRIED TO COLLECTION |  |  |  | 0
A3.6 ARCHIVE / RECORDS STORAGE
A | Heavy-duty steel shelving bays. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Lockable steel filing/storage cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Map/plan cabinet (if required by Annex B). | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Step stool/ladder. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Sorting worktable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.6 Archive / Records Storage — CARRIED TO COLLECTION |  |  |  | 0
A3.7 GUARD POST
A | Desk/counter. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Lockable cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.7 Guard Post — CARRIED TO COLLECTION |  |  |  | 0
A3.8 ANCILLARY
A | Staff lockers. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Kitchenette/tea-point units and fittings where shown on the approved design. | TBC | SET | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Waste bins. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Window blinds/curtains to all offices and the meeting room. | TBC | SM | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Wall clocks. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
F | First-aid cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — A3.8 Ancillary — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART A3 — JOWHAR FURNITURE
| A3.1 Offices (Technical And Administrative Staff) |  |  |  | 0
| A3.2 Gis / Data-Processing Workstation Area |  |  |  | 0
| A3.3 Meeting / Training Room |  |  |  | 0
| A3.4 Reception / Waiting Area |  |  |  | 0
| A3.5 Server / Ict Room (Racks Are Under Part A2) |  |  |  | 0
| A3.6 Archive / Records Storage |  |  |  | 0
| A3.7 Guard Post |  |  |  | 0
| A3.8 Ancillary |  |  |  | 0
| TOTAL — PART A3 — JOWHAR FURNITURE — CARRIED TO SUMMARY |  |  |  | 0

## A4 Jowhar Installation
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART A — JOWHAR IMC — A4 INSTALLATION AND INTEGRATION (Component D, Tender 6.11/6.17)
Installation, integration, configuration and interconnection of all Equipment and systems into a functioning whole, by trained personnel to manufacturers' instructions, coordinated across trades (suppression interlocks, UPS-fed cooling controls, ATS signalling).
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
A4.1 STRUCTURED CABLING (Tender 6.11)
A | Category 6A horizontal cabling from server-room patch panels to data outlets in every office, workstation position, meeting/training room, reception and guard post, including outlets, faceplates, labelling and containment separate from power — per outlet point. | TBC | POINT | TBC |  | Added: outlets per room NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Fibre-optic backbone where shown on the ICT Drawings, with termination, patching and testing. | TBC | M | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | External ducting to the perimeter/guard post for data and CCTV cabling. | TBC | M | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | ICT containment (trunking, trays, conduits), separated from power cabling. | TBC | M | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Certification testing of every link with a calibrated tester; test results, labelling schedule and as-built cabling schematics. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — A4.1 Structured cabling — CARRIED TO COLLECTION |  |  |  | 0
A4.2 SERVER-ROOM FIT-OUT AND INTEGRATION
A | Installation of racks, PDUs, environmental monitoring, cable management; coordination with raised floor, cooling, suppression, access control and clean earth. | 1 | ITEM | TBC |  | Added: rate TBC
B | Installation of servers, storage, backup device and KVM; installation of operating systems, database, GIS and analysis software; configuration and hardening. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — A4.2 Server room — CARRIED TO COLLECTION |  |  |  | 0
A4.3 NETWORK AND CONNECTIVITY
A | Installation and configuration of switches, firewall/router and Wi-Fi: VLANs, addressing, basic security, internet termination point; network documentation. | 1 | ITEM | TBC |  | Added: rate TBC
B | Installation and configuration of workstations, laptops, printers/plotter, scanner and meeting-room AV; user set-up. | 1 | ITEM | TBC |  | Added: rate TBC
C | Configuration of data-collection tools and their synchronisation with the server platform; coordination with FAO SWALIM for application software and data migration. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — A4.3 Network — CARRIED TO COLLECTION |  |  |  | 0
A4.4 BUILDING-SERVICES EQUIPMENT INSTALLATION
A | Installation of the standby generator, ATS and UPS, including connection, interlocks and controls. | 1 | ITEM | 0 | 0 | Modified: original 'generator connection, testing and commissioning' split: installation here, commissioning under A5 — REVIEW rate
B | Installation of precision-cooling and split AC units with pipework, drains, controls and electrical connection. | 1 | ITEM | TBC |  | Added: rate TBC
C | Installation of fire detection/alarm and clean-agent suppression systems with interlocks to cooling and power. | 1 | ITEM | TBC |  | Added: rate TBC
D | Installation of CCTV and access-control systems, including door hardware and integration with the fire alarm for egress. | 1 | ITEM | TBC |  | Added: rate TBC
E | Installation of water-supply pumps, tanks and controls. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — A4.4 Equipment installation — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART A4 — JOWHAR INSTALLATION AND INTEGRATION
| A4.1 Structured cabling |  |  |  | 0
| A4.2 Server room |  |  |  | 0
| A4.3 Network |  |  |  | 0
| A4.4 Equipment installation |  |  |  | 0
| TOTAL — PART A4 — JOWHAR INSTALLATION AND INTEGRATION — CARRIED TO SUMMARY |  |  |  | 0

## A5 Jowhar Services
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART A — JOWHAR IMC — A5 SERVICES: TESTING, COMMISSIONING, DOCUMENTATION, HANDOVER AND MAINTENANCE SUPPORT (Component E, Tender 6.17–6.20)
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
A5.1 TESTING AND COMMISSIONING (Tender 6.17)
A | Pre-commissioning inspections and static tests: insulation resistance, earth resistance and lightning-protection tests, polarity, pressure tests, cable certification. | 1 | ITEM | 0 | 0 | Modified: original 'testing of earth resistance and LPS' (USD 300) absorbed here — REVIEW rate for wider scope
B | Functional tests per system: generator load test (load bank or building load), ATS transfer/re-transfer, UPS autonomy on battery, cooling capacity and alarms, fire zone tests and suppression integrity test without discharge, CCTV/access-control tests, water-supply and pump tests. | 1 | ITEM | TBC |  | Added: rate TBC
C | Integrated systems test: simulated mains failure with server room loaded (ATS/generator/UPS and cooling continuity), fire/suppression interlocks, and end-to-end functional demonstration of the IMC (field data captured, transferred, processed, analysed and disseminated) witnessed by FAO SWALIM. | 1 | ITEM | TBC |  | Added: Tender 6.17 'fully functional'; rate TBC
D | Witnessed acceptance tests with the Supervisor and Employer/SWALIM; signed test certificates; snagging and completion of snag list. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — A5.1 Testing and commissioning — CARRIED TO COLLECTION |  |  |  | 0
A5.2 DOCUMENTATION AND HANDOVER (Tender 6.20)
A | As-built architectural, structural, electrical, mechanical and ICT drawings (hard copy and editable electronic). | 1 | SET | TBC |  | Added: rate TBC
B | O&M manuals for every system with preventive-maintenance schedules; test certificates; warranties in the Employer's name; key schedule. | 1 | SET | TBC |  | Added: rate TBC
C | Asset register of all Equipment and Furniture with serial numbers and asset tags; cable-certification reports and network documentation. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — A5.2 Documentation — CARRIED TO COLLECTION |  |  |  | 0
A5.3 WARRANTY AND MAINTENANCE SUPPORT (Tender 6.18, SCC)
A | Defects Liability Period 12 months and equipment warranties (min. 12 months) — warranty administration and defects rectification response within 7 days. | 1 | ITEM | TBC |  | Added: rate TBC
B | Maintenance support for 12 months from Taking-Over: scheduled preventive-maintenance visits for generator, UPS, cooling, fire and security systems at manufacturers' intervals, and call-out service with response within 3 working days. | 12 | MONTH | TBC |  | Added: rate TBC
| TOTAL — A5.3 Maintenance support — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART A5 — JOWHAR SERVICES
| A5.1 Testing and commissioning |  |  |  | 0
| A5.2 Documentation |  |  |  | 0
| A5.3 Maintenance support |  |  |  | 0
| TOTAL — PART A5 — JOWHAR SERVICES — CARRIED TO SUMMARY |  |  |  | 0

## A6 Jowhar Training
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART A — JOWHAR IMC — A6 TRAINING AND CAPACITY BUILDING (Component F, Tender 6.16)
Training of Employer-nominated staff before Taking-Over, in English with Somali interpretation, by equipment suppliers or the Contractor's qualified specialists using the installed systems; training materials (printed and electronic), attendance records, training report and certificates. Number of trainees and duration per module: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED (Tender 6.16 refers to this BOQ part).
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
A6.1 TRAINING MODULES
A | Building and services operation: building systems, water supply, sanitation, drainage, general electrical, air-conditioning, routine inspections. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Backup power: generator start-up/shut-down, ATS operation, fuelling, routine maintenance, fault response, UPS operation and battery care. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Server room and cooling: precision-cooling operation, environmental monitoring, alarm response, housekeeping rules. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | Fire and security: fire alarm and suppression operation, evacuation, extinguisher use; CCTV and access-control administration. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | ICT administration: network configuration and documentation, patching, server/storage basics, backup routine, user administration, data-collection tools and analysis software. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Training materials, attendance records, training report and certificates of attendance. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — A6.1 Training modules — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART A6 — JOWHAR TRAINING
| A6.1 Training modules |  |  |  | 0
| TOTAL — PART A6 — JOWHAR TRAINING — CARRIED TO SUMMARY |  |  |  | 0

## B0-B1 Kismayo Design&Works
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART B — KISMAYO IMC — B0 DETAILED DESIGN AND B1 WORKS (Component A: Design and Works)
Quantities are the Employer's indicative quantities for a single-storey IMC taken from the original BOQ (one building); the Contractor verifies them against its approved design (design-and-build, Tender 6.3). Kismayo, Jubaland State (coastal): all external metalwork, roofing, fixings, fencing, gates and external electrical enclosures corrosion-protected for a saline marine environment (hot-dip galvanised, marine-grade coatings or stainless steel); roofing engineered for coastal wind loads; concrete cover and mix designed for chloride exposure; borehole water tested for salinity (Tender 6.7).
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
B0 DETAILED DESIGN (Tender 6.3, SCC 4.4)
A | Detailed architectural design: site layout, floor plans, elevations, sections, schedule of finishes, doors/windows, furniture layout, signage — signed by the registered Architect; submission within 21 days of Commencement and revisions until approval. | 1 | ITEM | TBC |  | Added: Tender 6.3 (design-and-build); rate TBC
B | Structural design: foundations based on the geotechnical report, superstructure, roof structure, calculations and design basis report — signed by the Structural Engineer. Coastal wind loads and chloride exposure. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
C | Electrical design: load schedule, single-line diagram, distribution, lighting, earthing and lightning protection, generator/ATS/UPS sizing and layout. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
D | Mechanical design: air-conditioning and precision-cooling loads and layouts, fire detection/suppression, plumbing, water supply, sanitation and stormwater drainage. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
E | ICT design: structured-cabling layout, server-room layout, network architecture, CCTV and access-control layouts, hardware/software configuration for a fully functional IMC. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
F | External-works design: perimeter security, guard post, car park, landscaping, drainage; shop drawings, coordination drawings, temporary-works design and as-built drawings. | 1 | ITEM | TBC |  | Added: Tender 6.3; rate TBC
| TOTAL — B0 Detailed design — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 1 — SUBSTRUCTURE (all work up to and including the ground-floor slab)
A | Clear site of grass, shrubs, bush and small trees; grub up roots; fill with selected soil; remove debris to an approved dump (no burning — Tender 6.14 environmental management). | 768 | SM | 0 | 0 | Modified: 'burn debris' removed (environmental requirement)
B | Excavate for column bases not exceeding 1.5 m from reduced level. | 89 | CM | 0 | 0 | Aligned
C | Excavate for foundation trench not exceeding 1.5 m deep from reduced level. | 195 | CM | 0 | 0 | Aligned
D | Return, fill and ram selected excavated material around foundations and below ground slabs in layers not exceeding 200 mm, compacted to 95% MDD. | 114 | CM | 0 | 0 | Aligned
E | Surplus excavated material: load, wheel, spread and level on site where directed. | 170 | CM | 0 | 0 | Aligned
F | 200 mm hardcore bed in broken stone minimum 75 mm, blinded, under floor bed and verandah. | 113.71 | CM | 0 | 0 | Aligned
G | Ditto, 100 mm under steps, ramps and landings (step-free access — Tender 6.6). | 5.3 | CM | 0 | 0 | Aligned
H | 50 mm sand blinding over hardcore. | 465 | SM | 0 | 0 | Aligned
I | Anti-termite treatment (Termidor EC 25 or equal and approved) to hardcore surfaces, top of foundation walling, excavation bottoms and sides, and made-up ground (Tender 6.7/6.8 termite protection). | 623 | SM | 0 | 0 | Aligned
| PLAIN IN-SITU CONCRETE CLASS 20 (min. mix 1:2:4, 20 mm aggregate, 0.5 w/c) in: |  |  | 0
J | 50 mm blinding under column bases and strip footings and to make up levels. | 95 | SM | 0 | 0 | Aligned
VIBRATED IN-SITU REINFORCED CONCRETE CLASS 20 (20 mm aggregate, 0.5 w/c, min. 400 kg cement/m³) — mix designed for chloride exposure with increased cover (Tender 6.7 Kismayo) in:
K | Column bases. | 22 | CM | 0 | 0 | Aligned
L | Strip footings. | 33 | CM | 0 | 0 | Aligned
M | Stub columns. | 2.48 | CM | 0 | 0 | Aligned
N | Ground beams. | 32 | CM | 0 | 0 | Aligned
O | 600 mm wide splash apron. | 52 | SM | 0 | 0 | Aligned
STEEL FABRIC REINFORCEMENT (A142 mesh, 2.22 kg/m²) in floor bed, verandah, splash aprons, ramps, landings, steps and stormwater channel, including tying wire and spacers:
P | A142 fabric mesh. | 631 | SM | 0 | 0 | Aligned
MILD STEEL ROUND BARS / HIGH-TENSILE RIBBED BARS, cut, bent, fixed:
Q | 8 mm diameter mild steel bars. | 1602 | KG | 0 | 0 | Aligned
R | 12 mm diameter high-tensile ribbed bars. | 3055 | KG | 0 | 0 | Aligned
FORMWORK to:
S | Sides of column bases. | 86 | SM | 0 | 0 | Aligned
T | Sides of strip footings. | 108 | SM | 0 | 0 | Aligned
U | Sides of stub columns. | 49 | SM | 0 | 0 | Aligned
V | Sides of ground beams. | 158 | SM | 0 | 0 | Aligned
W | Vertical sides of ramp and landing, average 125 mm wide, cut to profile. | 3 | SM | 0 | 0 | Aligned
X | Vertical sides of steps, average 150 mm girth. | 8 | SM | 0 | 0 | Aligned
DAMP-PROOF MEMBRANE (Tender 6.7/6.8 damp-proofing):
Y | 1000-gauge polythene DPM in one layer with 300 mm laps on blinded hardcore to floor bed, verandah, splash apron, ramps and landings. | 615 | SM | 0 | 0 | Aligned
WALLING below ground:
Z | 400 mm thick approved natural stone foundation walling in cement/sand (1:3) mortar. | 126.24 | CM | 0 | 0 | Aligned
| TOTAL — Element 1 Substructure — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 2 — REINFORCED CONCRETE FRAME
VIBRATED IN-SITU REINFORCED CONCRETE CLASS 20 (20 mm aggregate, min. 400 kg cement/m³) in:
A | Roof/ring beams. | 13 | CM | 0 | 0 | Aligned
B | Lintels. | 5.9 | CM | 0 | 0 | Aligned
C | Columns. | 7 | CM | 0 | 0 | Aligned
STEEL REINFORCEMENT, cut, bent, hoisted and fixed, including tying wire and spacers:
D | 8 mm diameter mild steel bars. | 961 | KG | 0 | 0 | Aligned
E | 12 mm diameter high-tensile ribbed bars. | 1226 | KG | 0 | 0 | Aligned
F | 14 mm diameter high-tensile ribbed bars. | 1016 | KG | 0 | 0 | Aligned
FORMWORK to:
G | Sides and soffits of ring/roof beams. | 252 | SM | 0 | 0 | Aligned
H | Sides and soffits of lintels. | 118 | SM | 0 | 0 | Aligned
I | Sides of columns. | 134 | SM | 0 | 0 | Aligned
| TOTAL — Element 2 RC frame — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 3 — WALLING
Solid concrete blockwork 5.0 N/mm² (samples and laboratory test results before proceeding — Tender 6.15 material approvals), jointed and pointed in cement/sand (1:4) mortar, with double hoop-iron ties every fourth course (Tender 6.8 concrete-block walling):
A | 200 mm thick walls. | 493 | SM | 0 | 0 | Aligned
B | 200 mm concrete vent blocks (3.5 N/mm²) bedded, jointed and pointed in cement/sand (1:4) mortar, finished in coloured cement. | 11 | SM | 0 | 0 | Aligned
| TOTAL — Element 3 Walling — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 4 — ROOFING, CEILING AND RAINWATER DISPOSAL
TIMBER TRUSSES — rates include gusset and base plates, stiffeners, bolts, cleats, drilling, concrete pockets, connections, treatment and painting, per the Contractor's approved structural design; trusses engineered for wind uplift and coastal wind loads (Tender 6.7); samples approved before mass production. The following in 4 No. trusses spanning approx. 9000 mm hoisted approx. 3500 mm above ground (Tender 6.8: steel or treated-timber trusses):
A | 150 x 50 mm treated top chords. | 344.4 | LM | 0 | 0 | Modified: 'treated' timber per Tender 6.8
B | 150 x 50 mm treated tie beams. | 299.4 | LM | 0 | 0 | Aligned
C | 150 x 50 mm treated ridge and valley members. | 228.8 | LM | 0 | 0 | Aligned
D | 100 x 50 mm treated struts and ties. | 244.7 | LM | 0 | 0 | Aligned
E | 100 x 50 mm purlins including 150 x 100 x 5 mm MS cleats on trusses. | 878.4 | LM | 0 | 0 | Aligned
F | 100 x 50 mm wall plate. | 146 | LM | 0 | 0 | Aligned
G | 200 x 200 x 5 mm MS plates with 4 holes for 16 mm anchor bolts, hot-dip galvanised (Tender 6.7 Kismayo). | 36 | NO | 0 | 0 | Aligned
H | 50 x 150 x 4 mm plates with 50 x 200 x 4 mm split cleats anchored into concrete pockets, hot-dip galvanised. | 36 | NO | 0 | 0 | Aligned
I | 12 mm diameter grade 4.6 anchor bolts 385 mm long with nuts and washers, hot-dip galvanised. | 36 | NO | 0 | 0 | Aligned
ROOF COVERING — 28-gauge pre-painted IT5 profiled metal roofing sheets fixed to purlins with J-bolts, marine-grade coating and stainless/galvanised fixings (Tender 6.7 Kismayo):
J | Sheeting laid sloping not exceeding 45° from horizontal. | 878 | SM | 0 | 0 | Aligned
K | Ridge capping to match. | 114.8 | LM | 0 | 0 | Aligned
L | Under-roof insulation to reduce internal heat gain (Tender 6.8) — reflective foil/insulation laid over purlins under sheeting. | 878 | SM | TBC |  | Added: Tender 6.8 under-roof insulation; qty taken as roof area; rate TBC
M | 200 x 25 mm wrot cypress fascia and barge boards fixed to trusses, three coats paint. | 168 | LM | 0 | 0 | Aligned
N | Ceiling: 1200 x 2400 x 6 mm commercial plywood panels fixed to trusses, three coats paint — to all rooms except the server room. | 448 | SM | 0 | 0 | Modified: 'for classrooms' (school template) → 'all rooms'; panel size 240 mm corrected to 2400 mm — REVIEW
O | Server-room ceiling: sealed, dust-free ceiling (e.g. moisture-resistant gypsum board, taped, sealed and painted), no water services above (Tender 6.8). | TBC | SM | TBC |  | Added: Tender 6.8 server-room finishes; area NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
RAINWATER DISPOSAL — uPVC gutters, downpipes and fittings (Marley or equal and approved) discharging to the stormwater drainage system (Tender 6.8):
P | 150 mm diameter gutters complete with brackets to timber fascia. | 166 | LM | 0 | 0 | Aligned
Q | Extra over for 150 mm gutter angles and swan-necks. | 16 | NO | 0 | 0 | Aligned
R | Extra over for 150 mm stop ends. | 14 | NO | 0 | 0 | Aligned
S | Extra over for 150 x 110 mm gutter outlets. | 28 | NO | 0 | 0 | Aligned
T | 110 mm diameter uPVC downpipes clipped to walls, cast below splash apron at bottom. | 60 | LM | 0 | 0 | Aligned
U | Extra over for 110 mm x 90° bends. | 10 | NO | 0 | 0 | Aligned
V | Extra over for 110 mm shoes cast below splash apron. | 10 | NO | 0 | 0 | Aligned
Prepare, prime and apply three coats gloss oil paint to:
W | Surfaces over 200 mm not exceeding 300 mm girth (fascia). | 200 | LM | 0 | 0 | Aligned
X | Surfaces not exceeding 100 mm girth. | 50 | LM | 0 | 0 | Aligned
Y | 110 mm diameter uPVC downpipes. | 50 | LM | 0 | 0 | Aligned
Z | Extra over for bends. | 56 | NO | 0 | 0 | Requires Review: 56 bends vs 10 bends in item above — original BOQ inconsistency
AA | Extra over for shoes. | 18 | NO | 0 | 0 | Requires Review: 18 shoes vs 10 shoes above — original BOQ inconsistency
| TOTAL — Element 4 Roofing and rainwater — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 5 — DOORS (Tender 6.8: security grilles/shutters and insect screening; solid-core/steel doors with access-controlled locks to server room and archive; fire-rated doors where required)
A | Main-entrance aluminium-framed glazed double doors with safety glazing, frames, handles, locks, hinges, closers and ironmongery, complete — marine-grade powder coating and stainless fixings (Kismayo). | 2 | NO | 0 | 0 | Aligned
B | Internal flush doors with hardwood/metal frames, architraves, hinges, lever handles, locks, stops and ironmongery, complete. | 14 | NO | 0 | 0 | Aligned
C | Fire-rated steel door and frame to the server room with fire-rated hardware, closer, lever hardware and lockset, prepared for the electronic access-control lock (Tender 6.8/6.9). | 1 | NO | 0 | 0 | Modified: prepared for access control per Tender 6.9
D | Solid-core or steel door and frame to the archive/records room with lockset, prepared for the electronic access-control lock (Tender 6.8/6.9). | 1 | NO | TBC |  | Added: Tender 6.8 archive door; rate TBC
E | External security shutters/grilles to external doors where required by the approved design. | TBC | SM | TBC |  | Added: Tender 6.8; extent NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 5 Doors — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 6 — WINDOWS
A | Powder-coated aluminium-framed glazed windows, sliding/casement, with clear glazing, handles, locks, stays, seals, perimeter sealant and accessories, complete — marine-grade finish and stainless fixings (Kismayo). | 78 | SM | 0 | 0 | Aligned
B | Burglar-proof steel security grilles to windows/openings, welded, anti-corrosion treated (hot-dip galvanised — Kismayo) and painted, complete. | 38 | SM | 0 | 0 | Aligned
C | Insect screening to all openable windows and external doors (Tender 6.8) — aluminium/fibreglass mesh in frames. | 78 | SM | TBC |  | Added: Tender 6.8; qty taken as window area; rate TBC
| TOTAL — Element 6 Windows — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 7 — WALL FINISHES
EXTERNAL — cement and washed sand (1:3) render, trowelled smooth:
A | 20 mm two-layer render to walls with flattened tyrolean finish in cement/washed sand (1:2). | 327 | SM | 0 | 0 | Aligned
B | Ditto to external skirting, average 200–300 mm wide. | 141 | LM | 0 | 0 | Aligned
EXTERNAL PAINTING — prepare and apply three coats first-grade weatherguard emulsion (waterproofing and damp-proofing appropriate to the climate — Tender 6.8):
C | Rendered/tyrolean walls and concrete surfaces. | 327 | SM | 0 | 0 | Unit Revised: LM → SM (area = render area)
D | Skirting 200–300 mm girth, external. | 141 | LM | 0 | 0 | Aligned
INTERNAL LIME PLASTER — first coat cement/lime/sand (1:2:9), second coat cement/lime putty/sand (1:1:6), steel-trowelled smooth:
E | 12 mm two-coat plaster to walls. | 624 | SM | 0 | 0 | Unit Revised: LM → SM
F | Plaster to internal skirting 200–300 mm girth. | 252 | LM | 0 | 0 | Unit Revised: SM → LM
| INTERNAL PAINTING — one mist coat and three coats silk vinyl emulsion on: |  |  | 0
G | Plastered wall surfaces. | 624 | SM | 0 | 0 | Aligned
H | Skirting 200–300 mm girth, internal. | 252 | LM | 0 | 0 | Aligned
I | Server room: sealed, dust-free wall finish — anti-dust epoxy/acrylic sealer coating over plaster (Tender 6.8). | TBC | SM | TBC |  | Added: Tender 6.8; area NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 7 Wall finishes — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 8 — FLOOR FINISHES
VIBRATED IN-SITU REINFORCED CONCRETE CLASS 20 in:
A | 125 mm thick ground-floor slab. | 83.13 | CM | 0 | 0 | Aligned: original formula 665 SM x 0.125 retained
B | Extra over floor bed for 25 mm power-floated topping with hardener, bonding agent and 25 mm ebonite strips at 2 x 2 m grid — floors generally, verandah, ramps and steps. | 665 | SM | 0 | 0 | Aligned
C | 150 x 25 mm cement/sand (1:3) verandah skirting, square top and coved bottom. | 53 | LM | 0 | 0 | Aligned
D | Ceramic floor tiles on cement/sand screed with matching skirting, to offices, reception, meeting/training room, corridors and sanitary areas per Schedule of Finishes. | 200 | SM | 0 | 0 | Modified: now included in element total (was excluded from original SUM range)
E | Raised access floor to the server room: 600 x 600 mm steel-encapsulated panels on adjustable pedestals, anti-static HPL finish, ramp/step at threshold, cut-outs for cabling (Tender 6.6/6.8). | TBC | SM | TBC |  | Added: Tender 6.8 raised floor; area NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 8 Floor finishes — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 9 — ELECTRICAL INSTALLATION WORKS (Tender 6.9). Generator, ATS and UPS are supplied under Part B2 and installed/commissioned under Parts B4/B5.
All materials supplied, delivered, installed, connected, tested and commissioned complete with fixing, mounting and terminating accessories per the approved design; suitable for the 415/240 V 50 Hz system; underground cables include excavation, sand bedding, ducts and backfilling; indoor cables concealed in conduits/trunking; fire detection fully addressable; installation tested to IEC 60364 / current IET Wiring Regulations (Tender 6.4) and witnessed by the Supervisor. All external enclosures corrosion-protected for a marine environment (Tender 6.7 Kismayo).
A | Connection to the mains supply as shown on the electrical Drawings, including metering, main incomer and supply-authority requirements (Tender 6.9). | 1 | ITEM | TBC |  | Added: Tender 6.9 mains connection; availability per Annex G; rate TBC
B | Main LV distribution board (MDB) with MCCBs, MCBs, residual-current protection, surge protection, busbars, metering, enclosure and accessories, with ATS incomer provision. | 1 | NO | 0 | 0 | Modified: RCD protection added per Tender 6.9
C | Sub-distribution boards with breakers, RCDs, surge protection, busbars, neutral/earth bars and accessories — including a dedicated UPS-fed board for the server room, cooling and ICT equipment (Tender 6.9 dedicated circuits). | 3 | NO | 0 | 0 | Modified: dedicated server-room/UPS board included in 3 No. — REVIEW
D | Distribution-board feeder cables with glands, lugs, terminations and supports. | 1 | ITEM | 0 | 0 | Unit Revised: NO → ITEM
E | Cable containment: trunking and cable trays with supports and accessories, separate from ICT containment. | 150 | M | 0 | 0 | Aligned
| POWER AND SOCKET OUTLETS: |  |  | 0
F | Twin 13 A switched socket outlets, flush, with wiring and accessories. | 50 | NO | 0 | 0 | Aligned
G | Dedicated 13 A socket outlets for IT/server equipment on UPS-fed circuits. | 20 | NO | 0 | 0 | Modified: UPS-fed per Tender 6.9
H | Weatherproof external socket outlets. | 6 | NO | 0 | 0 | Aligned
I | Isolator switches for dedicated equipment (AC units, precision cooling, pumps). | 10 | NO | 0 | 0 | Aligned
LIGHTING (internal LED lighting, external and perimeter security lighting — Tender 6.9):
J | LED recessed/panel light fittings approx. 36–40 W with drivers and accessories. | 70 | NO | 0 | 0 | Aligned
K | LED surface-mounted light fittings for service areas. | 20 | NO | 0 | 0 | Aligned
L | LED external/security light fittings to building perimeter. | 12 | NO | 0 | 0 | Aligned
M | LED perimeter/fence security lighting on poles or wall brackets with photocell control (Tender 6.6/6.9). | TBC | NO | TBC |  | Added: Tender 6.6 perimeter external lighting; qty NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
N | Lighting switches, 1-way/2-way as required. | 25 | NO | 0 | 0 | Aligned
O | Lighting control wiring, conduits and accessories. | 1 | ITEM | 0 | 0 | Aligned
WIRING AND CONDUITING:
P | PVC/LSZH conduits, concealed or surface, with bends, boxes, saddles and accessories. | 1000 | M | 0 | 0 | Aligned
Q | Lighting-circuit wiring complete with cables, conduits and terminations. | 1200 | M | 0 | 0 | Aligned
R | Socket/power-circuit wiring complete with cables, conduits and terminations. | 1500 | M | 0 | 0 | Aligned
S | Sub-main cables between MDB and distribution boards. | 300 | M | 0 | 0 | Aligned
T | Cable glands, lugs, ferrules, connectors, junction boxes and miscellaneous accessories. | 1 | ITEM | 0 | 0 | Requires Review: USD 10,000 lump for sundries appears high relative to the installation — REVIEW rate
GENERATOR AND ATS BUILDER'S WORK AND CABLING (equipment under Part B2):
U | Generator-to-ATS/MDB power cable, glands, lugs and terminations. | 1 | ITEM | 0 | 0 | Aligned
V | Reinforced-concrete generator plinth, secure ventilated enclosure/canopy base, exhaust routing and bunded fuel-storage area (Tender 6.9). | 1 | ITEM | TBC |  | Added: Tender 6.9 generator location; rate TBC
EARTHING AND LIGHTNING PROTECTION (Tender 6.9):
W | Main building earthing system: electrodes, earth pits, copper/GI conductors and connections. | 1 | ITEM | 0 | 0 | Aligned
X | Dedicated clean earth for the server room and ICT equipment, bonded to the main earth (Tender 6.9). | 1 | ITEM | TBC |  | Added: Tender 6.9 clean earth; rate TBC
Y | Equipotential bonding to MDB, DBs and metallic services. | 1 | ITEM | 0 | 0 | Aligned
Z | Lightning-protection system: air terminals, down conductors, earth electrodes, test clamps and accessories. | 1 | ITEM | 0 | 0 | Aligned
EMERGENCY AND SAFETY LIGHTING:
AA | Emergency LED fittings with integral battery backup. | 15 | NO | 0 | 0 | Aligned
AB | Illuminated EXIT signs with battery backup (fire-exit signage — Tender 6.9). | 8 | NO | 0 | 0 | Aligned
AC | External emergency/security lighting and controls. | 1 | ITEM | 0 | 0 | Aligned
| TOTAL — Element 9 Electrical works — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 10 — WATER SUPPLY, SANITATION AND DRAINAGE (Tender 6.10)
A | Borehole: drilling, casing, screening, gravel pack, development and test pumping, wellhead, submersible pump, rising main, cabling and controls, with water-quality test including salinity, and treatment as necessary (Tender 6.7 Kismayo) — where the borehole is the water source per the mechanical Drawings. | 1 | NO | TBC |  | Added: Tender 6.10; depth/yield NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED; delete if network connection applies
B | Connection to the municipal/private water network with meter and isolation valve — where applicable per the mechanical Drawings. | 1 | ITEM | TBC |  | Added: Tender 6.10 alternative source; rate TBC
C | Water storage: elevated and/or ground storage tank(s) with support structure, booster/transfer pump, float controls, pipework and valves (Tender 6.6/6.10). | 1 | ITEM | TBC |  | Added: capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | Piped water supply: cold-water piping, valves, meters and fittings to sanitary facilities and external taps (retained from original 'Piped supply systems'). | 1 | ITEM | 0 | 0 | Modified: description aligned; rate retained but REVIEW (was a lump 'as per drawings')
E | Sanitary fittings: WCs, wash-hand basins, urinals, taps, mirrors, dispensers and accessories for male, female and accessible facilities, including accessible WC grab rails and step-free access (Tender 6.6/6.10). | 1 | SET | TBC |  | Added: numbers of fittings NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Foul drainage and disposal: sanitary drainage pipes, fittings, traps, manholes, cleanouts and septic tank with soakaway or connection to sewer as applicable (retained from original 'Disposal systems', aligned). | 1 | ITEM | 0 | 0 | Modified: septic tank/soakaway explicit; rate retained but REVIEW
G | Stormwater drainage: surface channels, gullies, pipes and outfall for roof, hardstanding and site. | 1 | ITEM | TBC |  | Added: Tender 6.10; extent NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — Element 10 Water and sanitation — CARRIED TO COLLECTION |  |  |  | 0
ELEMENT 11 — EXTERNAL WORKS AND PERIMETER SECURITY (Tender 6.6/6.8)
A | Perimeter wall or fence to the height and type in the approved design, galvanised/marine-coated metalwork (Kismayo). | TBC | LM | TBC |  | Added: type/height/length NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Vehicle gate, steel, with locks — hot-dip galvanised. | 1 | NO | TBC |  | Added: Tender 6.6; rate TBC
C | Pedestrian gate, steel, with lock. | 1 | NO | TBC |  | Added: Tender 6.6; rate TBC
D | Guard post / security screening point at the main gate, complete with finishes, door, window, lighting and power. | 1 | NO | TBC |  | Added: Tender 6.6; size NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Car park and hardstanding: sub-base, base and surfacing with kerbs and markings. | TBC | SM | TBC |  | Added: capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Paved paths and step-free access routes. | TBC | SM | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
G | Landscaping with drought-tolerant planting and topsoil. | TBC | SM | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
H | Building identification signage in English and Somali as instructed by the Employer (Tender 6.8). | 1 | NO | TBC |  | Added: rate TBC
| TOTAL — Element 11 External works — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART B0–B1 — KISMAYO DESIGN AND WORKS
| B0 Detailed design |  |  |  | 0
| Element 1 Substructure |  |  |  | 0
| Element 2 RC frame |  |  |  | 0
| Element 3 Walling |  |  |  | 0
| Element 4 Roofing and rainwater |  |  |  | 0
| Element 5 Doors |  |  |  | 0
| Element 6 Windows |  |  |  | 0
| Element 7 Wall finishes |  |  |  | 0
| Element 8 Floor finishes |  |  |  | 0
| Element 9 Electrical works |  |  |  | 0
| Element 10 Water and sanitation |  |  |  | 0
| Element 11 External works |  |  |  | 0
| TOTAL — PART B0–B1 — KISMAYO DESIGN AND WORKS — CARRIED TO SUMMARY |  |  |  | 0

## B2 Kismayo Supplies
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART B — KISMAYO IMC — B2 SUPPLIES: HARDWARE, SOFTWARE AND TOOLS (Component B)
All equipment new, of current production, supported by the manufacturer in the region, with manufacturer's warranty (min. 12 months), manuals and datasheets; licences in the Employer's name (Tender 6.12). Ratings and quantities per Annex B — where Annex B does not yet state them they are marked TBC.
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
B2.1 BACKUP POWER (Tender 6.9)
A | Standby diesel generator set, rating per Annex B, sound-attenuated canopy, automatic start on mains failure, control panel, starter battery, exhaust, base/day fuel tank of capacity per Annex B, and accessories. | 1 | NO | 0 | 0 | Modified: sound-attenuated canopy, auto-start and fuel tank added per Tender 6.9; rating not specified — rate REVIEW
B | Automatic transfer switch (ATS) with enclosure, controls and load-shedding provision for non-essential circuits. | 1 | NO | 0 | 0 | Aligned
C | UPS, on-line double-conversion, rating and autonomy per Annex B, sealed maintenance-free batteries, bypass and monitoring, for the server room and critical loads. | 1 | NO | TBC |  | Added: Tender 6.9; rating NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — B2.1 Backup power — CARRIED TO COLLECTION |  |  |  | 0
B2.2 AIR-CONDITIONING AND PRECISION COOLING (Tender 6.9)
A | Precision-cooling units for the server room sized to the IT heat load, N+1 redundancy, with temperature/humidity monitoring and alarms. | TBC | NO | TBC |  | Added: number/capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Split air-conditioning units for offices, workstation area, meeting/training room and reception, capacities per mechanical Drawings. | TBC | NO | TBC |  | Added: number/capacity NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — B2.2 Cooling — CARRIED TO COLLECTION |  |  |  | 0
B2.3 FIRE DETECTION AND SUPPRESSION (Tender 6.9)
A | Addressable fire detection and alarm system: control panel at reception/guard post, detectors, manual call points, sounders, cabling and batteries, zoned per the approved design. | 1 | SET | TBC |  | Added: number of devices NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Clean-agent (gaseous) suppression system for the server room with cylinders, nozzles, pipework, pre-discharge warning, abort switch and interlocks to cooling and power; agent per mechanical Specifications. | 1 | SET | TBC |  | Added: agent/room volume NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Portable fire extinguishers of appropriate type with brackets and signage, to all areas. | TBC | NO | TBC |  | Added: number NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — B2.3 Fire — CARRIED TO COLLECTION |  |  |  | 0
B2.4 SECURITY SYSTEMS (Tender 6.9)
A | CCTV system: cameras covering perimeter, gates, entrances, reception, workstation area and server-room door; network video recorder with not less than 30 days' retention; monitoring display at guard post/reception; cabling and PoE. | 1 | SET | TBC |  | Added: number of cameras NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Electronic access-control system at the main entrance, server room and archive: controllers, readers, electric locks, door hardware, cards/credentials and software with audit logging. | 3 | DOOR | TBC |  | Added: Tender 6.9: three controlled doors; rate TBC
| TOTAL — B2.4 Security — CARRIED TO COLLECTION |  |  |  | 0
B2.5 SERVER ROOM, NETWORK AND ICT HARDWARE (Tender 6.11/6.12)
A | Lockable 42U server racks with PDUs fed from the UPS, cable management and accessories. | TBC | NO | TBC |  | Added: number NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Environmental monitoring (temperature, humidity, water leak, door) with alarms. | 1 | SET | TBC |  | Added: rate TBC
C | Rack servers. | TBC | NO | TBC |  | Added: specification/number NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | Network-attached storage or SAN. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Backup device/media. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Rack-mounted KVM. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
G | Core/distribution switches. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
H | Edge/access switches (PoE). | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
I | Firewall/router. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
J | Wi-Fi access points covering all working areas. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
K | Patch panels, patch cords and rack accessories. | 1 | SET | TBC |  | Added: rate TBC
L | GIS/data-processing workstations, high specification, with dual monitors. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
M | Office desktop computers with monitors. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
N | Laptops. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
O | Multifunction printers/copiers. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
P | Large-format plotter/scanner for maps (if required by Annex B). | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
Q | Document scanner. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
R | Meeting/training room AV: projector or large-format display, screen, sound system, video-conferencing unit. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — B2.5 ICT hardware — CARRIED TO COLLECTION |  |  |  | 0
B2.6 SOFTWARE AND LICENCES (Tender 6.11/6.12) — licences issued in the Employer's name
A | Server operating systems and client access licences. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Workstation operating systems. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Database software. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | GIS software (desktop and server) and data-analysis software. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Office productivity suite. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Antivirus/endpoint security. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
G | Backup software. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — B2.6 Software — CARRIED TO COLLECTION |  |  |  | 0
B2.7 TOOLS FOR DATA COLLECTION AND ANALYSIS (Tender 6.12)
A | Handheld GPS units. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Field data-collection tablets / rugged devices with protective cases. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Survey and measurement tools for field data collection. | TBC | SET | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | External storage drives and media. | TBC | NO | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
| TOTAL — B2.7 Data-collection tools — CARRIED TO COLLECTION |  |  |  | 0
B2.8 SPARE PARTS AND CONSUMABLES (Tender 6.12/6.18)
A | Manufacturers' recommended spare parts and consumables for the first 12 months of operation for generator, UPS, cooling, fire, security and ICT systems, with spare-parts list and local supplier contacts. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — B2.8 Spares — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART B2 — KISMAYO SUPPLIES
| B2.1 Backup power |  |  |  | 0
| B2.2 Cooling |  |  |  | 0
| B2.3 Fire |  |  |  | 0
| B2.4 Security |  |  |  | 0
| B2.5 ICT hardware |  |  |  | 0
| B2.6 Software |  |  |  | 0
| B2.7 Data-collection tools |  |  |  | 0
| B2.8 Spares |  |  |  | 0
| TOTAL — PART B2 — KISMAYO SUPPLIES — CARRIED TO SUMMARY |  |  |  | 0

## B3 Kismayo Furniture
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART B — KISMAYO IMC — B3 FURNITURE AND OFFICE FITTINGS (Component C, Tender 6.13)
Commercial/office-grade furniture for continuous institutional use; laminated/veneered moisture-resistant tops with sealed edges; powder-coated steel or hardwood frames; cleanable upholstery; all cabinets/pedestals/lockers lockable with two keys, keyed differently and recorded in a key schedule; delivered assembled or assembled on site, levelled and fixed; min. 12-month warranty; every item asset-tagged. Kismayo: materials suitable for a saline coastal environment. Quantities per Annex B / furniture layout — TBC where not yet stated.
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
B3.1 OFFICES (technical and administrative staff)
A | Office desk with lockable drawer pedestal. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Ergonomic office chair: height adjustment, tilt, lumbar support, armrests, swivel. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Visitor chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Lockable steel filing cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Bookshelf/storage cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.1 Offices (Technical And Administrative Staff) — CARRIED TO COLLECTION |  |  |  | 0
B3.2 GIS / DATA-PROCESSING WORKSTATION AREA
A | Staff workstation/computer table sized for dual monitors, with cable management and CPU holder. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Ergonomic operator chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Mobile pedestal, lockable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Shared lockable storage unit. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.2 Gis / Data-Processing Workstation Area — CARRIED TO COLLECTION |  |  |  | 0
B3.3 MEETING / TRAINING ROOM
A | Modular meeting/conference table for the number of persons on the furniture layout. | TBC | SET | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Meeting/training chairs, stackable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Presenter's table/lectern. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Whiteboard and flip-chart stand. | TBC | SET | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Storage cabinet for training materials. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.3 Meeting / Training Room — CARRIED TO COLLECTION |  |  |  | 0
B3.4 RECEPTION / WAITING AREA
A | Reception desk/counter with lockable storage. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Receptionist chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Visitor seating: waiting benches/sofa units. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Coffee table. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Notice board. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.4 Reception / Waiting Area — CARRIED TO COLLECTION |  |  |  | 0
B3.5 SERVER / ICT ROOM (racks are under Part B2)
A | Technician's worktable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Technician's stool/chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Lockable storage cabinet for ICT spares, tools and media. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Wall-mounted document holder for network documentation. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.5 Server / Ict Room (Racks Are Under Part B2) — CARRIED TO COLLECTION |  |  |  | 0
B3.6 ARCHIVE / RECORDS STORAGE
A | Heavy-duty steel shelving bays. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Lockable steel filing/storage cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Map/plan cabinet (if required by Annex B). | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Step stool/ladder. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Sorting worktable. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.6 Archive / Records Storage — CARRIED TO COLLECTION |  |  |  | 0
B3.7 GUARD POST
A | Desk/counter. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Chair. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Lockable cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.7 Guard Post — CARRIED TO COLLECTION |  |  |  | 0
B3.8 ANCILLARY
A | Staff lockers. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
B | Kitchenette/tea-point units and fittings where shown on the approved design. | TBC | SET | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
C | Waste bins. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
D | Window blinds/curtains to all offices and the meeting room. | TBC | SM | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
E | Wall clocks. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
F | First-aid cabinet. | TBC | NO | TBC |  | Added: Tender 6.13; qty per Annex B/furniture layout
| TOTAL — B3.8 Ancillary — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART B3 — KISMAYO FURNITURE
| B3.1 Offices (Technical And Administrative Staff) |  |  |  | 0
| B3.2 Gis / Data-Processing Workstation Area |  |  |  | 0
| B3.3 Meeting / Training Room |  |  |  | 0
| B3.4 Reception / Waiting Area |  |  |  | 0
| B3.5 Server / Ict Room (Racks Are Under Part B2) |  |  |  | 0
| B3.6 Archive / Records Storage |  |  |  | 0
| B3.7 Guard Post |  |  |  | 0
| B3.8 Ancillary |  |  |  | 0
| TOTAL — PART B3 — KISMAYO FURNITURE — CARRIED TO SUMMARY |  |  |  | 0

## B4 Kismayo Installation
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART B — KISMAYO IMC — B4 INSTALLATION AND INTEGRATION (Component D, Tender 6.11/6.17)
Installation, integration, configuration and interconnection of all Equipment and systems into a functioning whole, by trained personnel to manufacturers' instructions, coordinated across trades (suppression interlocks, UPS-fed cooling controls, ATS signalling).
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
B4.1 STRUCTURED CABLING (Tender 6.11)
A | Category 6A horizontal cabling from server-room patch panels to data outlets in every office, workstation position, meeting/training room, reception and guard post, including outlets, faceplates, labelling and containment separate from power — per outlet point. | TBC | POINT | TBC |  | Added: outlets per room NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Fibre-optic backbone where shown on the ICT Drawings, with termination, patching and testing. | TBC | M | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | External ducting to the perimeter/guard post for data and CCTV cabling. | TBC | M | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | ICT containment (trunking, trays, conduits), separated from power cabling. | TBC | M | TBC |  | Added: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | Certification testing of every link with a calibrated tester; test results, labelling schedule and as-built cabling schematics. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — B4.1 Structured cabling — CARRIED TO COLLECTION |  |  |  | 0
B4.2 SERVER-ROOM FIT-OUT AND INTEGRATION
A | Installation of racks, PDUs, environmental monitoring, cable management; coordination with raised floor, cooling, suppression, access control and clean earth. | 1 | ITEM | TBC |  | Added: rate TBC
B | Installation of servers, storage, backup device and KVM; installation of operating systems, database, GIS and analysis software; configuration and hardening. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — B4.2 Server room — CARRIED TO COLLECTION |  |  |  | 0
B4.3 NETWORK AND CONNECTIVITY
A | Installation and configuration of switches, firewall/router and Wi-Fi: VLANs, addressing, basic security, internet termination point; network documentation. | 1 | ITEM | TBC |  | Added: rate TBC
B | Installation and configuration of workstations, laptops, printers/plotter, scanner and meeting-room AV; user set-up. | 1 | ITEM | TBC |  | Added: rate TBC
C | Configuration of data-collection tools and their synchronisation with the server platform; coordination with FAO SWALIM for application software and data migration. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — B4.3 Network — CARRIED TO COLLECTION |  |  |  | 0
B4.4 BUILDING-SERVICES EQUIPMENT INSTALLATION
A | Installation of the standby generator, ATS and UPS, including connection, interlocks and controls. | 1 | ITEM | 0 | 0 | Modified: original 'generator connection, testing and commissioning' split: installation here, commissioning under B5 — REVIEW rate
B | Installation of precision-cooling and split AC units with pipework, drains, controls and electrical connection. | 1 | ITEM | TBC |  | Added: rate TBC
C | Installation of fire detection/alarm and clean-agent suppression systems with interlocks to cooling and power. | 1 | ITEM | TBC |  | Added: rate TBC
D | Installation of CCTV and access-control systems, including door hardware and integration with the fire alarm for egress. | 1 | ITEM | TBC |  | Added: rate TBC
E | Installation of water-supply pumps, tanks and controls. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — B4.4 Equipment installation — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART B4 — KISMAYO INSTALLATION AND INTEGRATION
| B4.1 Structured cabling |  |  |  | 0
| B4.2 Server room |  |  |  | 0
| B4.3 Network |  |  |  | 0
| B4.4 Equipment installation |  |  |  | 0
| TOTAL — PART B4 — KISMAYO INSTALLATION AND INTEGRATION — CARRIED TO SUMMARY |  |  |  | 0

## B5 Kismayo Services
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART B — KISMAYO IMC — B5 SERVICES: TESTING, COMMISSIONING, DOCUMENTATION, HANDOVER AND MAINTENANCE SUPPORT (Component E, Tender 6.17–6.20)
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
B5.1 TESTING AND COMMISSIONING (Tender 6.17)
A | Pre-commissioning inspections and static tests: insulation resistance, earth resistance and lightning-protection tests, polarity, pressure tests, cable certification. | 1 | ITEM | 0 | 0 | Modified: original 'testing of earth resistance and LPS' (USD 300) absorbed here — REVIEW rate for wider scope
B | Functional tests per system: generator load test (load bank or building load), ATS transfer/re-transfer, UPS autonomy on battery, cooling capacity and alarms, fire zone tests and suppression integrity test without discharge, CCTV/access-control tests, water-supply and pump tests. | 1 | ITEM | TBC |  | Added: rate TBC
C | Integrated systems test: simulated mains failure with server room loaded (ATS/generator/UPS and cooling continuity), fire/suppression interlocks, and end-to-end functional demonstration of the IMC (field data captured, transferred, processed, analysed and disseminated) witnessed by FAO SWALIM. | 1 | ITEM | TBC |  | Added: Tender 6.17 'fully functional'; rate TBC
D | Witnessed acceptance tests with the Supervisor and Employer/SWALIM; signed test certificates; snagging and completion of snag list. | 1 | ITEM | TBC |  | Added: rate TBC
| TOTAL — B5.1 Testing and commissioning — CARRIED TO COLLECTION |  |  |  | 0
B5.2 DOCUMENTATION AND HANDOVER (Tender 6.20)
A | As-built architectural, structural, electrical, mechanical and ICT drawings (hard copy and editable electronic). | 1 | SET | TBC |  | Added: rate TBC
B | O&M manuals for every system with preventive-maintenance schedules; test certificates; warranties in the Employer's name; key schedule. | 1 | SET | TBC |  | Added: rate TBC
C | Asset register of all Equipment and Furniture with serial numbers and asset tags; cable-certification reports and network documentation. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — B5.2 Documentation — CARRIED TO COLLECTION |  |  |  | 0
B5.3 WARRANTY AND MAINTENANCE SUPPORT (Tender 6.18, SCC)
A | Defects Liability Period 12 months and equipment warranties (min. 12 months) — warranty administration and defects rectification response within 7 days. | 1 | ITEM | TBC |  | Added: rate TBC
B | Maintenance support for 12 months from Taking-Over: scheduled preventive-maintenance visits for generator, UPS, cooling, fire and security systems at manufacturers' intervals, and call-out service with response within 3 working days. | 12 | MONTH | TBC |  | Added: rate TBC
| TOTAL — B5.3 Maintenance support — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART B5 — KISMAYO SERVICES
| B5.1 Testing and commissioning |  |  |  | 0
| B5.2 Documentation |  |  |  | 0
| B5.3 Maintenance support |  |  |  | 0
| TOTAL — PART B5 — KISMAYO SERVICES — CARRIED TO SUMMARY |  |  |  | 0

## B6 Kismayo Training
DESIGN, CONSTRUCTION, SUPPLY, INSTALLATION AND EQUIPPING OF SWALIM INFORMATION MANAGEMENT CENTRES IN JOWHAR AND KISMAYO
Tender Ref. MOECC/UGBAAD/GCP-SOM-083-GCF/IMC/2026/01 — Annex A: Bill of Quantities
PART B — KISMAYO IMC — B6 TRAINING AND CAPACITY BUILDING (Component F, Tender 6.16)
Training of Employer-nominated staff before Taking-Over, in English with Somali interpretation, by equipment suppliers or the Contractor's qualified specialists using the installed systems; training materials (printed and electronic), attendance records, training report and certificates. Number of trainees and duration per module: NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED (Tender 6.16 refers to this BOQ part).
ITEM | DESCRIPTION | QTY | UNIT | RATE (USD) | AMOUNT (USD) | ALIGNMENT NOTE / STATUS
B6.1 TRAINING MODULES
A | Building and services operation: building systems, water supply, sanitation, drainage, general electrical, air-conditioning, routine inspections. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
B | Backup power: generator start-up/shut-down, ATS operation, fuelling, routine maintenance, fault response, UPS operation and battery care. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
C | Server room and cooling: precision-cooling operation, environmental monitoring, alarm response, housekeeping rules. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
D | Fire and security: fire alarm and suppression operation, evacuation, extinguisher use; CCTV and access-control administration. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
E | ICT administration: network configuration and documentation, patching, server/storage basics, backup routine, user administration, data-collection tools and analysis software. | TBC | DAY | TBC |  | Added: duration/trainees NOT SPECIFIED IN TENDER DOCUMENT – REVIEW REQUIRED
F | Training materials, attendance records, training report and certificates of attendance. | 1 | SET | TBC |  | Added: rate TBC
| TOTAL — B6.1 Training modules — CARRIED TO COLLECTION |  |  |  | 0
COLLECTION — PART B6 — KISMAYO TRAINING
| B6.1 Training modules |  |  |  | 0
| TOTAL — PART B6 — KISMAYO TRAINING — CARRIED TO SUMMARY |  |  |  | 0

## Gap Analysis
BOQ – TENDER GAP / ALIGNMENT ANALYSIS
Baseline: Tender Document (Design, Construction, Supply, Installation and Equipping of SWALIM IMCs in Jowhar and Kismayo). Original BOQ: 'Information Management Centre IMC - BOQ REVISED.xlsx'.
No. | BOQ Item | Tender Requirement | Difference / Issue | Action Taken | Status
1 | Whole BOQ — structure | Section 7: Part A Jowhar (A0–A6), Part B Kismayo (B0–B6), Part C General, Combined Summary; six components | Original covers ONE building (sheets: Preliminaries, Main Building, Solar, Summary); no site split, no components | Restructured into Part A / Part B / Part C with A0–A6 and B0–B6 sheets and a Combined Summary; building quantities duplicated for Kismayo | Modified
2 | Project title / references | Title, Tender Ref., Employer, project symbol GCP/SOM/083/GCF | Sheet headers linked to an external file ('[1]Fly Sht. Bill No. 1') — broken links; no title | Title, Tender Ref. and Employer inserted on every sheet; external links removed | Modified
3 | Bill No. 3 — Solar system (18 x 460 Wp modules, 8 batteries, 5 kVA hybrid inverter, MPPT, cables, 'for 1 school') | Tender 6.3 Exclusions / 6.9: no solar PV; backup power = generator + ATS + UPS | Entire bill unsupported; also school-template text | Sheet removed in full; UPS added to A2/B2.1 | Removed
4 | Preliminaries — 'Architect', 'Quantity Surveyor', 'consultants' | GCC 4.1: Supervisor administers the Contract | Terminology from a consultant-led school contract | Replaced by 'Supervisor' | Modified
5 | Preliminaries — 'B.S.' definition; 'British Standard current at date of Tender' | Tender 6.4: Employer's Requirements → Somali regulations → ISO/IEC or equivalent | Standards precedence differs | Definition aligned to Tender 6.4 | Modified
6 | Preliminaries — Nominated sub-contractors, nominated suppliers, P.C. sums | SCC: no nominated subcontractors; specialist subcontractors with approval; no P.C. sums | Unsupported provisions | Replaced by specialist-subcontractor clause | Modified
7 | Preliminaries — 'Copyright vested in Freshmind Consulting Company Limited' | Not in Tender | Consultant's copyright notice from a previous project | Removed | Removed
8 | Preliminaries — 'Training Levy: not applicable'; 'Shs' currency; 'USHS' rate header | TDS 2.13: USD | Currency and levy references from another country's form | Removed / corrected to USD | Removed
9 | Preliminaries — Lighting/power (10,000), Water (7,000), Transport (15,000) | Two sites | Priced once for one site | Quantity 2 SITE at the retained rate; flagged for review | Quantity Revised
10 | Preliminaries — Taxes 'as required by law' | TDS 2.12: prices inclusive of all taxes | Not explicit | Clause aligned | Modified
11 | Preliminaries — missing items | Mobilisation, securities, insurances (SCC 4.13), HSES/C-ESMP, environmental management, security compliance (Annex 10), QA/QC plan, reporting, key personnel, geotechnical provisional sum, permits | Absent from original | Added as Part C2 with rates TBC | Added
12 | Main Building — 'Clear site … burn debris' | Tender 6.14 environmental management | Burning prohibited by environmental requirements | Reworded to removal to approved dump | Modified
13 | Main Building — Element 1–3 (substructure, frame, walling) | Tender 6.8: RC foundations with DPM and termite treatment; RC frame; concrete-block walling; Kismayo chloride exposure; Jowhar flood levels | Broadly consistent; no site-specific notes | Retained with quantities and rates; site-specific notes added to Kismayo/Jowhar bills | Aligned
14 | Roofing — 'IT5 sheets on timber trusses', ceiling 'for classrooms' | Tender 6.8: profiled metal sheeting on steel or treated-timber trusses engineered for wind uplift, under-roof insulation; Kismayo coastal wind/corrosion | Insulation missing; school text; ceiling panel size '240mm' is a typo | Insulation item added (TBC rate); 'classrooms' → 'all rooms'; treated timber; galvanised plates/bolts for Kismayo; server-room ceiling added | Modified / Added
15 | Roofing — rainwater bends 56 / shoes 18 vs 10 / 10 above | — | Internal quantity inconsistency in original | Retained and flagged | Requires Review
16 | Doors — 2 entrance, 14 internal, 1 fire-rated server door | Tender 6.8: server room AND archive with solid-core/steel doors and access-controlled locks; grilles/shutters | Archive door missing; no access-control preparation; shutters missing | Archive door added (1 No.); server door prepared for access control; shutters added TBC | Added / Modified
17 | Windows — 78 SM glazing, 38 SM grilles | Tender 6.8: security grilles/shutters and insect screening | Insect screening missing | Screening added, qty = window area, rate TBC | Added
18 | Wall finishes — units (LM for wall painting/plaster; SM for skirting) | Measurement consistency | Units wrong in original | Corrected to SM/LM | Unit Revised
19 | Wall finishes — chalkboards, chalk rail, blackboard paint (items I–M) | Not in Tender (school template) | Unsupported | Removed | Removed
20 | Wall finishes — server room | Tender 6.8: sealed, dust-free walls and ceiling | Missing | Added, area TBC | Added
21 | Floor finishes — floor tiles 200 SM excluded from element total | — | Original SUM range F270:F276 omitted row 283 | Included in element total | Modified
22 | Floor finishes — raised access floor | Tender 6.6/6.8: raised access floor with anti-static finish to server room | Missing | Added, area TBC | Added
23 | Electrical — MDB/DBs, sockets, lighting, wiring, generator, ATS, earthing, LPS, emergency lighting | Tender 6.9 | Mostly consistent; missing mains connection, RCDs, UPS-fed dedicated board, clean earth, generator plinth/fuel bund, perimeter lighting | Retained with rates; missing items added (rates TBC); generator/ATS moved to Supplies A2/B2 with rates retained; 'IEE 16th Edition' updated | Modified / Added
24 | Electrical — sundries lump USD 10,000 | — | Appears high | Retained, flagged | Requires Review
25 | Electrical — feeder cables unit 'NO' | — | Should be ITEM | Corrected | Unit Revised
26 | Other services — 2 lumps of USD 10,000 'as per drawings' | Tender 6.10: borehole or network connection, storage tanks and pumps, sanitary fittings (male/female/accessible), septic tank/soakaway or sewer, stormwater drainage | Scope not itemised; borehole, tanks, sanitary fittings, stormwater missing | Lumps retained and re-described (rates flagged); missing items added TBC | Modified / Added
27 | External works | Tender 6.6/6.8: perimeter wall/fence, gates, guard post, car park, paths, landscaping, signage (English/Somali) | Entirely missing | Element 11 added, quantities TBC | Added
28 | Detailed design | Tender 6.3 / SCC 4.4 (design-and-build) | Missing | A0/B0 added | Added
29 | UPS, precision cooling, split AC, fire detection/suppression, extinguishers, CCTV, access control | Tender 6.9 | Entirely missing | A2/B2.1–2.4 added, quantities/ratings TBC | Added
30 | Server racks, servers, storage, network, workstations, peripherals, AV | Tender 6.11/6.12 | Entirely missing | A2/B2.5 added, TBC | Added
31 | Software/licences; tools for data collection and analysis; spares | Tender 6.11/6.12/6.18; work-plan wording | Entirely missing | A2/B2.6–2.8 added, TBC | Added
32 | Furniture | Tender 6.13 (room-by-room list and quality requirements) | Entirely missing | A3/B3 added with all Tender items, quantities TBC | Added
33 | Structured cabling Cat6A, fibre, ICT containment, certification | Tender 6.11 | Entirely missing | A4/B4.1 added, TBC | Added
34 | Installation and integration of equipment/ICT | Tender 6.17 | Only generator connection existed | A4/B4.2–4.4 added; generator item split | Added / Modified
35 | Testing and commissioning, integrated test, functional demonstration | Tender 6.17 | Only earth/LPS test (USD 300) | A5/B5.1 added | Added
36 | As-builts, O&M manuals, asset register, warranties | Tender 6.20 | Missing | A5/B5.2 added | Added
37 | 12-month maintenance support, defects response | Tender 6.18 / SCC | Missing | A5/B5.3 added | Added
38 | Training | Tender 6.16 | Missing | A6/B6 added; durations/trainees TBC (Tender defers to BOQ) | Added
39 | Summary — contingency 5% | Lump-sum contract (TDS 2.12) | Contingency in a lump-sum BOQ needs Employer decision | Retained, flagged | Requires Review
40 | Summary — Bill 4 'Other services' listed separately from Main Building total | — | Double-listing risk | Water/sanitation now Element 10 inside Part A1/B1 | Modified

## Outstanding Issues
OUTSTANDING ISSUES REQUIRING HUMAN REVIEW BEFORE ISSUE OF ANNEX A
No. | Issue | Where
1 | Confirm that the original single-building quantities (768 m² site clearance, 665 m² floor, 878 m² roof, 14 internal doors, etc.) represent the Employer's concept design for BOTH Jowhar and Kismayo. If the two IMCs differ in size, revise the Part B building quantities. | A1 / B1 Elements 1–9
2 | Annex B (FF&E and ICT Equipment Schedule) does not yet exist: every TBC quantity in Parts A2/B2 (equipment ratings, servers, workstations, software, tools), A3/B3 (furniture) and A4/B4 (cabling points) must be populated from it. Until then the Grand Total is incomplete. | A2–A4 / B2–B4
3 | Generator kVA, fuel-tank capacity, UPS kVA/autonomy, precision-cooling capacity and redundancy, suppression agent, number of cameras/access doors — Tender refers to Annex B/Employer's Requirements; none stated yet. | A2/B2.1–2.4
4 | Water source per site (borehole vs network) and sanitation (septic vs sewer) — both alternatives are carried; delete the one that does not apply at each site. | Element 10
5 | Server-room area, raised-floor area, wall/ceiling sealing areas — need the concept floor plan. | Elements 4, 7, 8
6 | Perimeter wall/fence type, height and length; car-park capacity; guard-post size; landscaping area. | Element 11
7 | Training: number of trainees per site and days per module — Tender 6.16 defers to this BOQ; the Employer must set them. | A6 / B6
8 | Rates flagged 'REVIEW': generator (USD 4,500 for an unspecified rating), electrical sundries (USD 10,000), the two USD 10,000 water/drainage lumps, preliminaries priced once but now applied to two sites, generator installation/commissioning split (USD 750 / 300). | various
9 | Original quantity inconsistencies retained and flagged: rainwater bends 56 vs 10, shoes 18 vs 10; ceiling panel '1200 x 240 mm' read as 1200 x 2400 mm. | Element 4
10 | Provisional sum for geotechnical investigation: amount to be set by the Employer (or delete if reports are issued for both sites). | Part C2
11 | Contingency 5% retained from the original Summary — decide whether a contingency/provisional-sum line is appropriate in a lump-sum contract (TDS 2.12). | Summary
12 | Timber roof trusses retained from the original; Tender 6.8 allows steel or treated timber. Confirm which is required for the coastal Kismayo site. | Element 4 (B1)
13 | Delete the 'Alignment note / status' column (G) on every sheet and the Gap Analysis / Outstanding Issues sheets before issuing Annex A to Bidders. | all sheets